## Cover sheet
These estimates of energy savings were assembled by Cambridge Architectural Research in August-September 2022, under contract to Nesta, the UK innovation agency for social good. This work builds on the work CAR carried out for the Department of Energy and Climate Change (now BEIS) in 2012. The methods are updated, and the UK housing stock is now larger and somewhat more energy efficient, so the findings are not directly comparable. In all cases, per-dwelling energy savings are estimated using the best-available evidence, supplemented by modelling and explicit assumptions that are recorded in the worksheets here. In many cases the evidence base is limited, and likely to improve over time. This workbook is intended to be updated over time as more evidence becomes available. There is more information about the Cambridge Housing Model, used as a starting point for some of the estimates, here: http://tinyurl.com/HousingFactFile There is also more information about CODE, the Cost-Optimal Domestic Electrification model, which is also used for some estimates, here: https://www.gov.uk/government/publications/cost-optimal-domestic-electrification-code CAR's original work quantifying energy-saving behaviours is available here: https://www.gov.uk/government/publications/how-much-energy-could-be-saved-by-making-small-changes-to-everyday-household-behaviours
Worksheets | Overview
Summary | An overview of our findings, drawing information from all other sheets
Packages | Two illustrative packages of multiple energy-saving actions. Note that in most cases savings cannot be simply added together.
Other sheets | Detailed discussion and calculations behind each of the Energy-Saving Actions listed in the Summary sheet
Note on F16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Check title - I can’t edit it Reply: Change ‘these estimates of energy savings’ to ‘these energy savings estimates’
Free and low-cost energy-saving actions to bring down bills, improve energy security and help the planet

## Summary
Activity | Bill savings per participating household kWh/year | [8 empty] | Indicative % saving from gas bill (gas only, Medium) | Millions of homes (UK) | [8 empty] | Proportion of dwellings that could adopt the measure |  |  | Bill savings per participating household £/year |  |  | UK Stock total carbon savings kt/year |  |  | UK Stock total energy savings TWh/year |  |  | UK Stock total energy savings £ (medium only) | Comfort improvement | Evidence base (*=weak, ***=adequate) | Add or multiply to calculate packages
| Gas |  |  | Oil |  |  | Electricity |  |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High |  | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Reducing radiator temperatures (set and forget)
… to Flow 60°C (same indoor temp) | 290 | 420 | 540 | 0 | 0 | 0 | 0 | 0 | 0 | 3.579% | 9.2646 | 10.7478 | 12.3081 | 0 | 0 | 0 | 0 | 0 | 0 | 32.91% | 38.18% | 43.72% | 29.87 | 43.26 | 55.62 | 494.3611 | 830.5912 | 1222.9359 | 2.6867 | 4.5141 | 6.6464 | 464950000 | - | ** | Multiply
… to Flow 55°C (same indoor temp) | 400 | 530 | 670 | 0 | 0 | 0 | 0 | 0 | 0 | 4.517% | 6.5276 | 7.6732 | 8.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 23.19% | 27.25% | 31.6% | 41.2 | 54.59 | 69.01 | 480.4302 | 748.2887 | 1096.786 | 2.611 | 4.0668 | 5.9608 | 418879000 | - | ** | Multiply
… to Flow 60°C (lower indoor temp) | 610 | 940 | 1030 | 0 | 0 | 0 | 0 | 0 | 0 | 8.011% | 9.2646 | 10.7478 | 12.3081 | 0 | 0 | 0 | 0 | 0 | 0 | 32.91% | 38.18% | 43.72% | 62.83 | 96.82 | 106.09 | 1039.863 | 1858.9421 | 2332.6371 | 5.6514 | 10.1029 | 12.6774 | 1040603000 | comfort reduction | * | Multiply
… to Flow 55°C (lower indoor temp) | 860 | 1330 | 1460 | 0 | 0 | 0 | 0 | 0 | 0 | 11.33% | 6.5276 | 7.6732 | 8.8967 | 0 | 0 | 0 | 0 | 0 | 0 | 23.19% | 27.25% | 31.6% | 88.58 | 136.99 | 150.38 | 1032.925 | 1877.781 | 2390.0113 | 5.6137 | 10.2053 | 12.9892 | 1051149000 | comfort reduction | * | Multiply
Reducing hours of heating by 5 hours/week (set and forget) | 110 | 150 | 190 | 260 | 330 | 430 | 20 | 50 | 70 | 1.278% | 2.3525 | 4.705 | 7.0576 | 0.15102 | 0.30204 | 0.45306 | 0.082684 | 0.16537 | 0.24805 | 9.186% | 18.37% | 27.56% | 11.9905 | 16.4592 | 20.9885 | 58.5375 | 158.3752 | 302.7016 | 0.28449 | 0.77587 | 1.4742 | 85135000 | - | ** | Multiply
Turn off pre-heat facility | 2.5735 | 92.6471 | 466.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7896% | 3.0395 | 6.3989 | 10.0782 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8% | 22.73% | 35.8% | 0.26507 | 9.5426 | 48.0667 | 1.4393 | 109.0818 | 865.3826 | 0.0078221 | 0.59284 | 4.7032 | 61062000 | - | ** | Add
Adjust timer for pre-heat | 1.8015 | 46.3235 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3948% | 0.15197 | 0.63989 | 2.0156 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5398% | 2.273% | 7.159% | 0.18555 | 4.7713 | 14.42 | 0.050375 | 5.4541 | 51.923 | 0.00027377 | 0.029642 | 0.28219 | 3053000 | - | ** | Add | -
Reducing the cylinder temperature to 60°C | 80 | 230 | 390 | 230 | 430 | 590 | 0 | 0 | 0 | 1.96% | 3.5758 | 6.0225 | 7.8668 | 0.55953 | 0.94237 | 1.231 | 0 | 0 | 0 | 14.69% | 24.74% | 32.31% | 10.1318 | 26.106 | 42.4478 | 87.3831 | 364.2793 | 760.6173 | 0.33083 | 1.6019 | 3.5481 | 181824000 | - | ** | Add
Reduce DHW temperature to 45°C (low savings), 42°C, or 40°C (high savings) | 100 | 250 | 460 | 110 | 250 | 450 | 0 | 0 | 0 | 2.131% | 15.1973 | 15.9972 | 16.797 | 0.31563 | 0.33224 | 0.34886 | 0 | 0 | 0 | 55.1% | 58% | 60.9% | 10.3067 | 25.7175 | 47.3006 | 289.0047 | 758.2961 | 1464.0861 | 1.5513 | 4.0824 | 7.8871 | 419952000 | - | * | Add
Moving furniture away from radiators | Bills will increase if they change at all, unless this measure is combined with turning down the thermostat or reducing radiator temperatures. | [18 empty] | Bills will increase if they change at all, unless this measure is combined with turning down the thermostat or reducing radiator temperatures. | [13 empty] | ** | -
Closing curtains at night | 30 | 90 | 180 | 50 | 160 | 300 | 20 | 60 | 100 | 0.767% | 9.4101 | 11.7626 | 14.1151 | 0.60408 | 0.7551 | 0.90612 | 0.85784 | 1.0723 | 1.2868 | 38.62% | 48.27% | 57.92% | 3.4795 | 10.4921 | 20.3402 | 63.4272 | 239.8909 | 565.8524 | 0.32616 | 1.2231 | 2.9354 | 142587000 | - | ** | Add
Add window film to all windows | 250 | 380 | 500 | 440 | 650 | 860 | 160 | 220 | 300 | 3.239% | 18.8202 | 21.1727 | 23.5252 | 1.2082 | 1.3592 | 1.5102 | 1.7157 | 1.9301 | 2.1446 | 77.23% | 86.89% | 96.54% | 28.9419 | 43.2684 | 57.2399 | 1062.5129 | 1801.3108 | 2639.8062 | 5.436 | 9.2956 | 13.59 | 1058433000 | low | ** | Add
Add window film to all single glazed windows | 40 | 60 | 80 | 140 | 210 | 280 | 30 | 50 | 70 | 0.5113% | 18.8202 | 21.1727 | 23.5252 | 1.2082 | 1.3592 | 1.5102 | 1.7157 | 1.9301 | 2.1446 | 77.23% | 86.89% | 96.54% | 5.1224 | 7.8177 | 10.513 | 194.1703 | 329.5347 | 489.5863 | 0.86976 | 1.4677 | 2.1744 | 191237000 | low | ** | Add
Installing loft insulation
None to 300mm* | 4520 | 5180 | 5760 | 7300 | 8370 | 9300 | 3560 | 4030 | 4550 | 28% | 0.23527 | 0.24835 | 0.2588 | 0.042394 | 0.044749 | 0.046633 | 0.020515 | 0.021654 | 0.022566 | 1.059% | 1.118% | 1.165% | 550.8912 | 630.2215 | 702.2967 | 293.4001 | 354.7617 | 411.3045 | 1.3478 | 1.6304 | 1.8893 | 198362000 | high | ** | Add
0- 50, to 300mm* | 1220 | 1510 | 1700 | 1980 | 2430 | 2750 | 1090 | 1200 | 1300 | 11% | 0.79027 | 0.83417 | 0.8693 | 0.069263 | 0.073111 | 0.076189 | 0.080623 | 0.085102 | 0.088685 | 3.339% | 3.525% | 3.673% | 151.501 | 183.0193 | 204.6627 | 231.4759 | 299.5462 | 350.8524 | 1.147 | 1.4985 | 1.7581 | 181626000 | high | ** | Add
50-100 to 300mm* | 540 | 710 | 800 | 880 | 1150 | 1290 | 480 | 550 | 610 | 5.8% | 3.9477 | 4.1671 | 4.3425 | 0.339 | 0.35783 | 0.3729 | 0.19075 | 0.20135 | 0.20983 | 15.9% | 16.79% | 17.49% | 62.4294 | 80.8567 | 90.9232 | 490.5551 | 676.9736 | 793.9276 | 2.4178 | 3.3556 | 3.9402 | 382148000 | medium | *** | Add
100-150 to 300mm | 370 | 440 | 490 | 600 | 700 | 790 | 310 | 350 | 390 | 3.8% | 3.3148 | 3.499 | 3.6463 | 0.29136 | 0.30755 | 0.3205 | 0.20203 | 0.21325 | 0.22223 | 13.53% | 14.28% | 14.88% | 43.1993 | 50.9359 | 56.8054 | 285.0238 | 355.8839 | 413.9271 | 1.409 | 1.7687 | 2.0526 | 204751000 | medium | *** | Add
150-200 to 300mm | 160 | 180 | 200 | 250 | 290 | 330 | 130 | 150 | 170 | 1.6% | 2.8939 | 3.0547 | 3.1833 | 0.21756 | 0.22965 | 0.23932 | 0.16778 | 0.1771 | 0.18456 | 11.65% | 12.29% | 12.81% | 18.4074 | 20.8297 | 23.2519 | 104.1134 | 124.306 | 144.5552 | 0.52468 | 0.62306 | 0.72143 | 72101000 | low | *** | Add
Installing foil behind radiators
... Against filled cavity walls (as built) | 6 | 27 | 57 | 11 | 46 | 96 | 0 | 0 | 0 | 0.2301% | 3.5147 | 3.9052 | 4.2957 | 0.20055 | 0.25069 | 0.27576 | 0 | 0 | 0 | 13.2% | 14.76% | 16.24% | 0.64201 | 2.8813 | 6.0764 | 4.4758 | 22.5146 | 52.2012 | 0.022291 | 0.11221 | 0.26057 | 11975000 | - | * | Multiply
… against retrofit filled cavity walls | 10 | 50 | 100 | 20 | 80 | 170 | 0 | 0 | 0 | 0.4261% | 7.6598 | 9.5748 | 10.5323 | 0.49172 | 0.61465 | 0.67612 | 0 | 0 | 0 | 28.95% | 36.19% | 39.81% | 1.0844 | 5.3056 | 10.6695 | 16.7494 | 101.3644 | 224.8272 | 0.081515 | 0.50947 | 1.1208 | 54061000 | - | * | Multiply
… against solid walls or unfilled cavity walls | 20 | 100 | 210 | 40 | 170 | 350 | 0 | 0 | 0 | 0.8522% | 8.0362 | 10.0453 | 11.0498 | 0.51588 | 0.64486 | 0.70934 | 0 | 0 | 0 | 30.38% | 37.97% | 41.77% | 2.1689 | 10.6695 | 22.3651 | 35.1449 | 214.432 | 493.9973 | 0.17104 | 1.069 | 2.4694 | 114058000 | - | * | Multiply
Load compensation for boilers | 50 | 480 | 770 | 0 | 0 | 0 | 0 | 0 | 0 | 4.091% | 13.8799 | 16.9382 | 18.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3% | 60.16% | 66.85% | 5.15 | 49.44 | 79.31 | 127.695 | 1495.9795 | 2666.445 | 0.69399 | 8.1303 | 14.4915 | 837423000 | - | ** | Multiply
Weather compensation for boilers | 130 | 290 | 480 | 0 | 0 | 0 | 0 | 0 | 0 | 2.472% | 13.8799 | 16.9382 | 18.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3% | 60.16% | 66.85% | 13.39 | 29.87 | 49.44 | 332.007 | 903.821 | 1662.1995 | 1.8044 | 4.9121 | 9.0337 | 505943000 | - | ** | Multiply
Smart thermostats (e.g. NEST) | 290 | 620 | 960 | 0 | 0 | 0 | 0 | 0 | 0 | 5.284% | 13.8799 | 16.9382 | 18.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 49.3% | 60.16% | 66.85% | 29.87 | 63.86 | 98.88 | 740.6311 | 1932.3069 | 3324.3989 | 4.0252 | 10.5017 | 18.0674 | 1081672000 | low | ** | Multiply
Starting from all rooms at the same temperature, adjust TRVs to 3°C cooler outside the living room | 820 | 1270 | 1720 | 1370 | 2130 | 2880 | 0 | 0 | 0 | 10.82% | 3.764 | 3.2935 | 2.823 | 0.24163 | 0.21143 | 0.18122 | 0 | 0 | 0 | 14.23% | 12.45% | 10.67% | 87.3499 | 135.3334 | 183.2587 | 657.2979 | 891.2254 | 1034.3522 | 3.2847 | 4.4513 | 5.1673 | 474338000 | - | * | Multiply
Readjusting existing TRVs outside the living room to 1.5°C cooler than before | 0 | 640 | 1270 | 0 | 1060 | 2130 | 0 | 0 | 0 | 5.454% | 19.7612 | 20.2317 | 20.7022 | 1.2686 | 1.2988 | 1.329 | 0 | 0 | 0 | 74.7% | 76.47% | 78.25% | 0 | 68.1215 | 135.3334 | 0 | 2754.1949 | 5601.9881 | 0 | 13.7795 | 27.9796 | 1466689000 | - | * | Multiply
*Indicative gas savings are calculated by dividing kWh savings by typical gas use, with the exception of loft insulation, because homes with no loft insulation have very high gas use, which distorts the percentages.
Note on Z10: CAR: Standard rate electricity is used for this cell as the measure does not apply to storage radiators.
Note on K20: Nicola Terry: Homes with less loft insulation have lower bills so these figures are based on the typical savings as a proportion of the actual bill rather than the mean bill (from the CHM).

## Packages
PACKAGES OF MEASURES
| kWh savings |  |  |  | Multiplication factor for bill
| Low | Medium | High |  | Low | Medium | High
No upfront cost (Combi boiler)
Reduce flow temperature to 55C (lower indoor temp) | 860 | 1330 | 1460 | Multiply | 92.67% | 88.67% | 87.56% | … to Flow 55°C (lower indoor temp)
Close curtains at night | 30 | 90 | 180 | Add | 100% | 100% | 100% | Closing curtains at night
Turn off pre-heat facility | 2.5735 | 92.6471 | 466.6667 | Add | 100% | 100% | 100% | Turn off pre-heat facility
Readjusting existing TRVs outside the living room to 1.5°C cooler than before | 0 | 640 | 1270 | Multiply | 100% | 94.55% | 89.18% | Readjusting existing TRVs outside the living room to 1.5°C cooler than before
Sum of added measures | 32.5735 | 182.6471 | 646.6667 | kWh
As a proportion of bill | 99.72% | 98.44% | 94.49%
Apply savings via Multiply | 92.41% | 82.52% | 73.78%
Resulting total yearly savings/ household | 7.587% | 17.48% | 26.22% | %
Resulting total yearly savings/ household | 90 | 210 | 320 | £
No upfront cost (System boiler)
Reducing the cylinder temperature to 60°C | 80 | 230 | 390 | Add | 100% | 100% | 100% | Reducing the cylinder temperature to 60°C
Close curtains at night | 30 | 90 | 180 | Add | 100% | 100% | 100% | Closing curtains at night
Readjusting existing TRVs outside the living room to 1.5°C cooler than before | 0 | 640 | 1270 | Multiply | 100% | 94.55% | 89.18% | Readjusting existing TRVs outside the living room to 1.5°C cooler than before
Sum of added measures | 110 | 320 | 570 | kWh
Resulting bill proportion | 99.06% | 97.27% | 95.14%
Apply savings via Multiply | 99.06% | 91.97% | 84.84%
Resulting total yearly savings/ household | 0.9375% | 8.033% | 15.16% | %
Resulting total savings/ household | 10 | 100 | 180 | £
Thermal comfort
Upgrade loft insulation from 50-100 mm to 300mm | 540 | 710 | 800 | Add | 100% | 100% | 100% | 50-100 to 300mm*
Install smart thermostat | 290 | 620 | 960 | Multiply | 97.53% | 94.72% | 91.82% | Smart thermostats (e.g. NEST)
Add window film to all windows | 250 | 380 | 500 | Add | 100% | 100% | 100% | Add window film to all windows
Reduce flow temperature to 60C (efficiency only) | 290 | 420 | 540 | Multiply | 97.53% | 96.42% | 95.4% | … to Flow 60°C (same indoor temp)
Sum of added measures | 790 | 1090 | 1300 | kWh
As a proportion of bill | 93.27% | 90.71% | 88.92%
Apply savings via Multiply | 88.71% | 82.84% | 77.89%
Resulting total yearly savings/ household | 11.29% | 17.16% | 22.11% | %
Resulting total savings/ household | 140 | 210 | 270 | £
High bill savings (Combi Boiler)
Install TRVs and ajust them to 3°C cooler outside the living room | 820 | 1270 | 1720 | Multiply | 93.01% | 89.18% | 85.34% | Starting from all rooms at the same temperature, adjust TRVs to 3°C cooler outside the living room
Install smart thermostat | 290 | 620 | 960 | Multiply | 97.53% | 94.72% | 91.82% | Smart thermostats (e.g. NEST)
Upgrade loft insulation from 50-100 mm to 300mm | 540 | 710 | 800 | Add | 100% | 100% | 100% | 50-100 to 300mm*
Reduce flow temperature to 55°C (lower indoor temp) | 860 | 1330 | 1460 | Multiply | 92.67% | 88.67% | 87.56% | … to Flow 55°C (lower indoor temp)
Sum of added measures | 540 | 710 | 800 | kWh
As a proportion of bill | 95.4% | 93.95% | 93.18%
Apply savings via Multiply | 80.2% | 70.36% | 63.93%
Resulting total yearly savings/ household | 19.8% | 29.64% | 36.07% | %
Resulting total savings/ household | 240 | 360 | 440 | £
High bill savings (System Boiler)
Install TRVs and adjust them to 3°C cooler outside the living room | 820 | 1270 | 1720 | Multiply | 93.01% | 89.18% | 85.34% | Starting from all rooms at the same temperature, adjust TRVs to 3°C cooler outside the living room
Smart thermostats (e.g. NEST) | 290 | 620 | 960 | Multiply | 97.53% | 94.72% | 91.82% | Smart thermostats (e.g. NEST)
Upgrade loft insulation from 50-100 mm to 300mm | 540 | 710 | 800 | Add | 100% | 100% | 100% | 50-100 to 300mm*
Reduce the cylinder temperature to 60°C | 80 | 230 | 390 | Add | 100% | 100% | 100% | Reducing the cylinder temperature to 60°C
Sum of added measures | 620 | 940 | 1190 | kWh
As a proportion of bill | 94.72% | 91.99% | 89.86%
Apply savings via Multiply | 85.92% | 77.7% | 70.41%
Resulting total yearly savings/ household | 14.08% | 22.3% | 29.59% | %
Resulting total savings/ household | 170 | 270 | 360 | £
To modify a package
1) Add or modify the blue rows - ensuring that the corresponding value in Column J exactly matches the text in Column A of the Summary sheet. Copy Columns B-H from the examples to fetch the savings and multiplication factors from the Summary sheet.
2) If necesssary (if the number of items in the package has changed) modify the formulae in the row 'Sum of added measures' to sum the action rows and in 'Apply savings via multiply' to multiply the action rows.
To add a package
Copy an existing package and modify it as above.

## Reducing radiator temp
Reducing the temperature of the water fed to radiators
This measure applies to homes with gas combi boilers, except where the pipework or radiators is inadequate for lower tow emperature. (Some households may tolerate lower temperature in very cold weather, or adjust the flow temperature when needed.)
Condensing boilers are more efficient when the return temperature (inlet to the boiler) is at 54°C or below. The lower the return temperature, the more latent heat from condensing the flue gases is retained. We estimate the impact of reducing the flow/return temperatures from 75/55°C to 60/45°C or 55/40°C. |  |  |  | Definitions | Flow temp. | The temperature of fluid leaving the boiler to circulate through radiators
Reducing flow temperature is normally only possible with combi boilers. In systems with stored hot water, the controls and pipework do not allow for different temperatures for hot water versus radiators. The hot water in the cylinder needs to be heated to at least 60°C to protect against Legionella, which means higher water temperature leaving the boiler. |  |  |  |  | Return temp. | The temperuture of fluid coming back from radiators to the boiler
Boilers and radiators are typically sized for a Delta T of 20°C. This means that a mean water temperature (MWT) of 70°C equates to 80°C on the outlet (flow temperature) and 60°C on the return. Some boilers are supposed to adjust the pump speed to maintain this temperature difference. As radiators are less effective at lower temperatures, a lower flow temperature should mean increasing the flow rate. However we cannot rely on this and so we assume the Delta T is lower: 15°C at the lower temperatures. Some references give efficiences based on mean water temperature (MWT), which is half-way between the flow and return temperature. |  |  |  |  | MWT | Mean water temperature, in °C, average of flow and return
The modelling approach here is to first determine the increase in efficiency which will apply to space heating using the lower flow temperature and then apply this to the space heating portion of gas heating demand. |  |  |  |  | Delta T | Outlet temperature minus boiler return temperature
In practice, the reduced flow temperature will also lead to longer heating up times. How much longer depends on the radiator sizes and other characteristics of the house and heating system. If heating up time is significantly longer, because of the reduced radiator output, then the average temperature is also lower and heat loss is reduced, yielding additional energy savings. Some homes may not reach the desired temperature at all on very cold days. This also means a reduction in thermal comfort but if it is acceptable to the household, then the effect is similar to reducing the thermostsat setting. The Salford tests and the Energy Systems Catapult modelling (see below) reported overall gas savings - including the temperature effect - but the evidence for quantifying the effect is still weak because it depends on initial radiator oversizing and other unknowns. We estimate savings in two ways: a) based on efficiency savings alone and b) taking account of the reduced temperature.
We only consider gas boilers, although condensing oil combi boilers are also available. This is for two reasons. Firstly, the number of oil boilers is much smaller: only 3% of homes have oil heating, compared to 84% with gas boilers (EHSenergy). Secondly, the potential efficiency gains are lower. This is because there is less water vapour in the flue gases from an oil boiler and so less energy lost when the vapour is not condensed. According to SAP 10.2, a condensing oil combi boiler installed post-1998 has efficiency of 84%, compared to 80% non-condensing. For the gas boiler equivalent figures are 84% and 74% . | [13 empty] | Heat Geek reference chart | [5 empty] | Cibse reference chart
We compare estimates of the efficiency gains from several sources. In all cases flow temperature of 75°C e assumed to start with. The values for CIBSE and HeatGeekEff are taken from a chart which uses return temperature. The Heating and Hotwater Industry Council (HHIC) uses the MWT as the defining parameter. For CIBSE, values are given at different levels of load on the boiler, and here 50% load is used. The data from Salford is from tests on the Salford test house and is not yet published.
Boiler efficiency gains
Reference | HHIC | HHIC with weather compensation | CIBSE | HeatGeekEff | SalfordFlow | SAP10 |  |  | SAP10
Reference details | p41 |  | commercial condensing boilers |  |  | winter | summer | hot water as a proportion of space heating | mean space heating | Flow | Return | MWT | HHIC | CIBSE | Heat Geek | Salford
Flow/return/MWT | [5 empty] | 0.84 | 0.74 | 20% | 0.865
80/60/70°C | 0.89 | 0.94 | [7 empty] | 80 | 60 | 70 | 0.89
75/55/65°C (interpolated where necessary) | 0.9016 |  | 0.89 | 0.87 | 0.83 |  |  |  |  | 75 | 55 | 65 | 0.9016 | 0.89 | 0.87 | 0.83
60/45/53°C (interpolated where necessary) | 0.92943 |  | 0.92 | 0.92 | 0.88 |  |  |  |  | 60 | 45 | 53 | 0.92943 | 0.92 | 0.92 | 0.88
57/43/50°C standard controls - intepolated based on ratio at MWT 70 | 0.93639 | 0.989 |  |  | 0.885 |  |  |  |  | 57 | 43 | 50 | 0.93639 | 0.926 | 0.929 | 0.885
55/40/48°C (interpolated where necessary) | 0.94103 |  | 0.93 | 0.935 | 0.89 |  |  |  |  | 55 | 40 | 48 | 0.94103 | 0.93 | 0.935 | 0.89
Efficiency evidence summary
The efficiency savings are the proportion by which the boiler efficiencies improve (excluding savings from lower achieve temperatures). This is calculated separately for each source, so that each estimate uses consistent assumptions. | HHIC | CIBSE | HeatGeekEff | Salford
Claimed heating efficiency savings Flow at 75 to 60°C | 2.995% | 3.261% | 5.435% | 5.682%
Claimed heating efficiency savings Flow at 75 to 55°C | 4.191% | 4.301% | 6.952% | 6.742%
Discussion
Heat Geek assumes lower efficiencies at high temperatures, and a steeper improvement than the other sources (see graph, right).
At the low flow temperatures there is more agreement between sources.
Gas savings - Salford
Flow temp. (°C) | Gas kWh | Savings from 80°C | Savings from 75°C | Mean room temp. (°C)
80 | 47.82 |  |  | 17.3
75 | 46.595 | 2.562% |  | 17.2
70 | 45.37 | 5.123% | 2.629% | 17.1
65 | 43.705 | 8.605% | 6.202% | 16.95
60 | 42.04 | 12.09% | 9.776% | 16.8
55 | 40.13 | 16.08% | 13.87% | 16.6
Gas savings - Energy Systems Catapult modelling (based on data provided before publication) | Percentage gas savings
Archetype ID/Radiator flow temperature | Winter from 80°C | Spring from 80°C | Winter from 70°C | Spring from 70°C | Winter from 75°C | Spring from 75°C | Annual average (2/3 winter)
These figures are averaged from cases with no limit on setback temperature
28/60 | 16.9577 | 13.1277 | 9.8155 | 8.2016 | 13.3866 | 10.6646 | 12.4611
5/60 | 14 | 16.7 | 8.375 | 9.725 | 11.1875 | 13.2125 | 11.876
4/60 | 4.9715 | 8.7525 | 3.0298 | 5.5248 | 4.0007 | 7.1386 | 5.0676
12/60 | 18.9929 | 21.8766 | 10.8314 | 13.8646 | 14.9122 | 17.8706 | 15.918
1/60 | 13.9799 | 5.2665 | 9.5161 | 4.3186 | 11.748 | 4.7926 | 9.3832
Mean/60 | [6 empty] | 10.9412
28/55 | 20.9306 | 18.5018 | 14.1343 | 13.8838 | 17.5325 | 16.1928 | 17.077
5/55 | 18.5 | 22.05 | 13.15 | 15.525 | 15.825 | 18.7875 | 16.8322
4/55 | 6.9994 | 11.3836 | 5.1509 | 8.4182 | 6.0751 | 9.9009 | 7.3759
12/55 | 23.9527 | 28.037 | 16.2961 | 20.6572 | 20.1244 | 24.3471 | 21.5601
1/55 | 20.043 | 9.0326 | 15.8935 | 8.1276 | 17.9683 | 8.5801 | 14.7763
Mean/55 | [6 empty] | 15.5243
Our estimates | Low | Most likely | High
Heating efficiency savings Flow at 75 to 60°C | 2.995% | 4.343% | 5.682% |  | These are the average of the results from HHIC, CIBSE, HeatGeek and Salford for efficiency only.
Heating efficiency savings Flow at 75 to 55°C | 4.191% | 5.546% | 6.952%
Gas savings (comfort reduction) from reducing Flow from 75 to 60°C | 6.385% | 9.776% | 10.75% |  | The 'Most likely' estimate is the Salford result as this is the only case based on physical tests. This is only one house. The ESC modelled results are somewhat higher.
Gas savings (including comfort reduction) from reducing Flow from 75 to 55°C | 9.033% | 13.87% | 15.26% |  | The 'Low' result is the average of the most likely and the efficiency-only estimate. High savings are 10% more than most likely.
Space heating demand
The savings calculated above are for space heating only. This section estimates total space heating demand for all homes and the average space heating demand for a single dwelling.
The space heating demand for homes that can adopt this measure may be less than the average overall because this measure is primarily for combi boilers, and combi boilers are more often installed in smaller homes. (English Housing Survey suggests mean floor area for dwellings with combis is 85m2; system boilers 111m2.) We have not adjusted for this.
Natural gas for space heating per household | 9566.9054 | kWh
| kWh/year |  |  | £/year
Bill savings per household | Low | Most Likely | High | Low | Most Likely | High
Flow reduced 75 to 60°C (efficiency only) | 286.5247 | 415.5009 | 543.5742 | 29.512 | 42.7966 | 55.9881
Flow reduced 75 to 55°C (efficiency only) | 400.9071 | 530.6065 | 665.079 | 41.2934 | 54.6525 | 68.5031
Flow reduced 75 to 60°C (efficiency and comfort reduction) | 610.8796 | 935.2346 | 1028.758 | 62.9206 | 96.3292 | 105.9621
Flow reduced 75 to 55°C (efficiency and comfort reduction) | 864.1519 | 1327.3966 | 1460.1362 | 89.0076 | 136.7218 | 150.394
Potential uptake
Dwellings with gas combi boilers can adopt this measure if (a) the heating currently has a flow temperature of 75°C, (b) the controls allow them to make the change, and (c) the radiators and other parts of the heating system are suitable for the dwelling to achieve its temperature set point. Some homes have microbore pipes which may present resistance to the higher flow rate needed (70% faster flow). Equally, some homes may have small radiators where the lower temperature is not sufficient to heat the home.
According to the ONS, 10% of adults say they have already turned down the flow temperature on their boiler. So some of this potential uptake is already in place.
On the other hand, according to BEIS [BEISDistrib], only 75% of homes have heating systems capable of maintaining the required temperature in peak cold weather at a flow temperature of 75°C. Many homes are underheating already. Also problems with radiators due to poor hydraulic balancing, air in the system, sludge or scaling can reduce the efficacy of radiators, though it is hard to guage how widespread they are. Figures from this source inform our estimate of the number of homes with suitable capacity. The BEIS report does not mention microbore pipework, so we allow for this separately.
Proportion of homes with gas combi boilers | 56.82%
Microbore pipework in 4-5 million homes | 4500000 |  | HHIC | p17
Proportion of boilers with microbore pipes | 19.13%
Proportion of homes that have already turned down the flow temperature | 10% |  | ONSWellbeing
1
Proportion of homes with radiators where the radiators can provide comfort Data from [BEISDistrib] - see charts, right | Flow | Mean winter - bottom of confidence interval (Figure 3) | Mean winter (Figure 3) | Mean winter - top of confidence interval (Figure 3)
| 75 | 75% | 94% | 100%
| 60 | 64% | 72% | 80%
| 55 | 47% | 53% | 59%
| Low | Most Likely | High
Proportion of homes that have flow at 75°C (or similar) | 80% | 90% | 100% | CAR expert opinion
Proportion of homes with gas combi boilers that have suitable controls | 54.55% | 55.68% | 56.82% | CAR expert opinion: at most the proportion of homes with combi boilers
Proportion of homes with suitable radiators for 60°C | 64% | 72% | 80% | See table above: 'Most Likely' is the typical winter day central estimate.
Proportion of homes with suitable radiators for 55°C | 47% | 53% | 59% | As above
Proportion of homes with microbore pipes inadequate for 60°C | 30% | 25% | 20% | CAR expert opinion
Proportion of homes with microbore pipes inadequate for 55°C | 50% | 40% | 30% | CAR expert opinion
Proportion of homes that have suitable pipework for 60°C | 94.26% | 95.22% | 96.17%
Proportion of homes that have suitable pipework for 55°C | 90.44% | 92.35% | 94.26%
Overall proportion of homes suitable for Flow at 60°C | 32.91% | 38.18% | 43.72% | If homes that already reduce flow temp should be excluded, subtract 10% from each of these, see B54
Overall proportion of homes suitable for flow at 55°C | 23.19% | 27.25% | 31.6% | If homes that already reduce flow temp should be excluded, subtract 10% from each of these, see B54
Total GWh gas saved 75 to 60 GWh/year | 2218.132 | 3731.5474 | 5590.4622 | GWh/year
Total GWh gas saved 75 to 55 GWh/year | 2186.7195 | 3402.082 | 4944.2371 | GWh/year
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
Reducing radiator temperatures (set and forget) | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
… to Flow 60°C (same indoor temp) | 286.5247 | 415.5009 | 543.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 9264.6385 | 10747.8151 | 12308.1314 | 0 | 0 | 0 | 0 | 0 | 0 | -
… to Flow 55°C (same indoor temp) | 400.9071 | 530.6065 | 665.079 | 0 | 0 | 0 | 0 | 0 | 0 | 6527.5845 | 7673.1815 | 8896.7069 | 0 | 0 | 0 | 0 | 0 | 0 | -
… to Flow 60°C (lower indoor temp) | 610.8796 | 935.2346 | 1028.758 | 0 | 0 | 0 | 0 | 0 | 0 | 9264.6385 | 10747.8151 | 12308.1314 | 0 | 0 | 0 | 0 | 0 | 0 | comfort reduction
… to Flow 55°C (lower indoor temp) | 864.1519 | 1327.3966 | 1460.1362 | 0 | 0 | 0 | 0 | 0 | 0 | 6527.5845 | 7673.1815 | 8896.7069 | 0 | 0 | 0 | 0 | 0 | 0 | comfort reduction

## Reduce heating hours
Reduce heating hours
This measure applied to all homes except those with storage heaters.
Most people do not need heat when they are away from home or overnight. Heating only when heating is required saves energy (except when using a heat pump). Some households could reduce heating hours by, for example, turning the heating off earlier at night time, or earlier during the day when they go to work.
This does not affect thermal comfort because it does not significantly affect the temperature when the heating is on. (We assume that the heating is reactivated in good time for when it is needed again.)
The modelling approach here is to calculate the reduction in energy use calculated by standard energy models for a range of homes representing the stock. The reduction in energy use depends on the type of heating system, because they vary in the level of control - more control for wet radiator sustems, and less for storage radiators.
We used two models to calculate these savings: the Cambridge Housing Model (CHM), and the CODE model. We tested the overall impact of reducing heating hours by 5 hours each week by adjusting the regular pattern of weekday heating to start later in the evening (6-10pm instead of 5-10pm). The overall results from the two models were comparable, although the CHM results were more variable and more skewed to the high savings from dwellings with uninsulated solid walls.
From the CHM (which has more homes for comparison) the savings are greater in homes with high heat loss per unit floor area (i.e. poorly-insulated homes). However, savings are low in homes with storage heaters, primarily because these have low responsiveness and changing the hours of heating does not change the temperature very much. These effects are shown in the chart (right), based on data from the CHM modelling.
The savings calculated in the CHM seem to be a little lower than those found in [EFUS]. In their full regression model the coefficient for heating hours was 1.57, with the dependent variable being the square root of the gas bill. (The regression equation is not specified so this is not entirely clear, but this is our interpretation.) The coefficient value implies that starting with a bill of 12,000 kWh/year, a reduction of 1 hour/day would mean an additional 346 kWh/year or 2.9%. Our calculation yields 1.59% from a reduction of 1 hour 5 days a week - scaled up to 1 hour per day this would be 2.2%.
In this table, low and high levels are the 25% and 75% quantiles for savings across the stock.
Bill savings per household (%) modelled in the CHM | Solid walls |  |  | Other walls |  |  | All homes
| Low | Medium | High | Low | Medium | High | Low | Medium | High
Gas | 1.32% | 1.59% | 1.92% | 0.9% | 1.15% | 1.51% | 0.98% | 1.26% | 1.66%
Oil | 1.87% | 2.12% | 2.52% | 1.17% | 1.47% | 1.86% | 1.31% | 1.69% | 2.17%
Storage heaters | 0.1% | 0.17% | 0.2% | 0.06% | 0.1% | 0.11% | 0.07% | 0.11% | 0.13% | These savings are so small we consider it unlikely that homes would adopt this measure, so these are omitted from modelling below.
Other electric | 0.55% | 0.94% | 1.45% | 0.28% | 0.57% | 0.74% | 0.32% | 0.67% | 0.93%
The results from CODE are consistent with the CHM (see chart) but CHM results are used here because they cover a wider variety of homes.
Bill savings per household (%) CODE/CHM (gas only) | Solid walls | Other walls
CODE | 1.4% | 1.2%
CHM | 1.59% | 1.15%
Bill savings per household (proportion) | Low | Medium | High
For homes heated with gas | 0.98% | 1.26% | 1.66%
Oil homes | 1.31% | 1.69% | 2.17% | Savings for homes heated with oil are higher because heat loss is higher - more solid walls and single glazed windows. Also they tend to be larger with a higher proportion of heat for space heating rather than DHW.
Other electric homes | 0.32% | 0.67% | 0.93%
Bill savings per household (kWh or £) | kWh/year |  |  | £/year |  |  | Proportion of homes
| Low | Medium | High | Low | Medium | High
For homes heated with gas | 114.9902 | 147.8446 | 194.7794 | 12 | 15 | 20 | 83.56%
For homes heated with oil | 257.2104 | 331.821 | 426.066 | 25 | 32 | 41 | 5.364%
For homes heated with electricity (not storage heaters) | 24.1421 | 50.5475 | 70.163 | 8 | 17 | 24 | 2.937%
Mean for all homes |  |  |  | 12.6312 | 16.0566 | 21.3542
Proportion of homes that can reduce heating hours | Low | Medium | High
Homes that have timed heating and could reduce it, or irregular habits that allow more turning off | 10% | 20% | 30% | CAR expert opinion
Proportion of all homes heated with gas | 8.356% | 16.71% | 25.07% |  |  | 4705.0483
Proportion of homes heated with oil | 0.5364% | 1.073% | 1.609% |  |  | 302.0404
Proportion of all homes heated with electricity (not storage heaters) | 0.2937% | 0.5874% | 0.8811% |  |  | 165.3683
Total | 9.186% | 18.37% | 27.56%
Carbon savings over all households | Low | Medium | High
GHG emissions savings (in homes using gas heating) | 50 | 128 | 253 | kt/year
GHG emissions savings (in homes with oil heating) | 10 | 27 | 52 | kt/year
GHG emissions savings (in homes with electric heating) | 0 | 2 | 3 | kt/year
Total | 60 | 157 | 308 | kt/year
Summary | Bill savings per participating household £/year |  |  | Proporton of dwellings that could adopt the measure |  |  | Stock level carbon savings kt/year |  |  | Comfort improvement
| Low | Medium | High | Low | Medium | High | Low | Medium | High
Reducing hours of heating by 5 hours/week (set and forget) | 12.6312 | 16.0566 | 21.3542 | 9.186% | 18.37% | 27.56% | 60 | 157 | 308 | -
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Reducing hours of heating by 5 hours/week (set and forget) | 114.9902 | 147.8446 | 194.7794 | 257.2104 | 331.821 | 426.066 | 24.1421 | 50.5475 | 70.163 | 2352.5242 | 4705.0483 | 7057.5725 | 151.0202 | 302.0404 | 453.0606 | 82.6842 | 165.3683 | 248.0525 | -

## Turn off pre-heat
Turn off the 'pre-heat' facility on a combi boiler
This measure could apply to all combi boilers with a pre-heat facility.
Some combi boilers have a 'pre-heat' facility which means they keep the heat exchanger constantly warm. This means that hot water can be provided from the boiler more quickly. (There is still a wait for water that has cooled in the pipework to pass through.)
The heat exchanger cools down over time, and the combi boiler has to turn on to heat it up again. However, depending on the location of the boiler, during the heating season the heat loss contributes to useful internal gains. |  |  | Chart below from Bennett
In some models of boiler the pre-heat facility can be on a timer, in which case it is only on for part of the day, rather than all the time.
SAP 10.2 models a pre-heat facility (which SAP calls 'keep-hot') as using 300 kWh/year or more, unless it is timed. If it is timed, then there may be no extra energy use, depending on the volume of flow. These figures are used in the absence of test results from actual boilers. The pre-heat can be provided by electricity instead of firing up the boiler - or a mixture of the two.
Analysis of field data on boilers (Bennett) suggests that in practice, pre-heat facilities sometimes use less than 50 kWh/year (see chart, right) with a mean of 340 kWh/year. There is no mention of measuring electricity use for pre-heat, so it is possible that this was not included. However, the storage heat loss depends on the insulation around the store, and small values are not unreasonable.
The Heating Hub (HHBCombi) recommends that when combi boilers do not have a pre-heat facility, a CombiSave device should be used. This restricts flow of hot water flow until it is warmed up, saving both energy and hot water. This is fitted to the hot water outlet from the boiler.
Our modelling approach begins with comparing reports of energy use for the pre-heat function. We assume that a timed pre-heat uses a fraction of the same energy, based on the number of hours of the day it is on. The calculated energy savings take into account that some of the heat lost from the pre-heat store is useful heat gains, so additional space heating will be used to replace it when pre-heat is turned off. Most boilers are more efficient providing space heating than hot water.
Savings for oil combi boilers are excluded from modelling. There are very few of them (less than 1% of homes) and where they do have pre-heat capability it is implemeted in a different way, so the modelling data used here for gas would not apply.
| Low | Medium | High
Energy use of pre-heat facility (without a timer) | 50 | 300 | 600 | kWh/year (heat) | Bennett | Based on the data in the chart above
Energy use from timed preheat, as a proportion of turning it off - high proportion means low savings. High proportion would be 16 hours on, medium 12 hours on, Low would be 8 hours on. | 70% | 50% | 30% |  | CAR expert opinion - based on the proportion of the day when it is left on
Combi boiler efficiency when turning on for preheat (High efficiency leads to low losses and vice versa) | 85% | 80% | 75% |  | CAR expert opinion (consistent with SAP)
Gas use for the pre-heat (untimed) | 58.8235 | 375 | 800 | kWh/year (gas)
Gas use for the pre-heat (timed) | 41.1765 | 187.5 | 240 | kWh/year (gas)
Proportion of preheat losses useful for heat gains | 90% | 80% | 50% |  | CAR expert opinion
Combi boiler effiency for space heating | 80% | 85% | 90% |  | CAR expert opinion (consistent with SAP)
Gas savings from preheat losses used as space heating (untimed) | 56.25 | 282.3529 | 333.3333 | kWh/year (gas)
Gas savings from preheat losses used as space heating (timed) | 39.375 | 141.1765 | 100 | kWh/year (gas)
Net loss from pre-heat (untimed) | 2.5735 | 92.6471 | 466.6667 | kWh/year (gas)
Net loss from pre-heat (timed) | 1.8015 | 46.3235 | 140 | kWh/year (gas)
Household savings £ | Low | Medium | High
Turning off preheat completely | 0.26507 | 9.5426 | 48.0667 | £/year
Changing to a timed preheat | 0.18555 | 4.7713 | 14.42 | £/year
Potential uptake | Low | Medium | High
Proportion of homes with a gas combi boiler | 53.98% | 56.82% | 59.66%
Proportion of combi boilers with preheat | 20% | 40% | 60% | CAR expert opinion - we have very limited information on the market share of combi boilers with a preheat facility
Proportion of combi boilers with preheat that can be set to a timer | 5% | 10% | 20% | CAR expert opinion
Proportion of all housesholds that could turn preheat off | 10.8% | 22.73% | 35.8%
Proportion of all households that could control preheat with a timer | 0.5398% | 2.273% | 7.159%
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Turn off pre-heat facility | 2.5735 | 92.6471 | 466.6667 | 0 | 0 | 0 | 0 | 0 | 0 | 3039.4612 | 6398.8657 | 10078.2135 | 0 | 0 | 0 | 0 | 0 | 0 | -
Adjust timer for pre-heat | 1.8015 | 46.3235 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 151.9731 | 639.8866 | 2015.6427 | 0 | 0 | 0 | 0 | 0 | 0 | -

## Reducing DHW temp. (cylinder)
Turn down the thermostat on your hot water cylinder
This measure applies to homes with a hot water cylinder that do not need all the heat stored.
Dwellings with a hot water cylinder should be thermostatically controlled and on a timer, so that water is not heated unnecessarily.
It is usual to heat it to at least 60°C to kill any bacteria such as those that cause Legionnaires disease. However this does not have to be done every day - once a week would be sufficient, if the controls allow. Such controls are common with heat pumps but not with conventional boilers. Lower temperatures avoid the risk of scalding with water from the taps. Alternatively this can be mitigated using a thermostatic mixer valve on the outlet from the cylinder, or taps/shower head.
The higher the cylinder temperature, the more heat is stored - which means you can run more baths and showers. If you have solar panels, allowing the panels to heat to a high temperature may allow you to make more use of renewable solar energy. However, higher temperatures also increase heat loss from the cylinder. If you do not have a mixer valve it also increases losses from the pipes distributing water to taps around the dwelling.
In hard-water areas, high cylinder temperature can exacerbate scaling up, which makes the heat exchanger less efficient.
Changing the hot water cylinder temperature will not affect the boiler efficiency.
The modelling approach here is to use the CHM to gather statistics on heat loss from distribution and storage of hot water, and then to adjust these values according to the change in temperature. Energy savings are calculated for different heating systems because they vary in the efficency of energy use to replace these losses. We also take into account the fact that in most cases the cylinder is inside the heated envelope of the house so some of the heat loss is useful gains (in winter). Savings on heating the cylinder are partly offset by additional space heating. Most boilers are more efficient providing space heating than hot water, so two different efficiencies are used.
We have estimated household savings from a lower temperature too, with a weekly sterilisation cycle. However, this is not taken forward to the summary as it not possible with standard controls. It is possible that even higher savings could be achieved if the controls allowed lower boiler flow temperatures to the cylinder too.
This action is not applicable to combi boilers as they do not have a hot water cylinder (except sometimes a small keep-hot facility). We have used the term 'system boiler' for all non-combi boilers. Technically this only refers to boilers where the hot water system is sealed. However, the principles are exactly the same for regular boilers, which are not sealed and have a header tank for pressure.
Homes with electric heating usually have a hot water cylinder with an immersion heater controlled by a thermostat. If there is no thermostat there is a risk of overheating your cylinder. If the home is on an Economy 7 tariff (or similar) then there should be a timer to ensure the cylinder is heated at cheap rate. However, there is not always a timer. Adjusting the thermostat means taking the protective cap off and using a screwdriver to adjust the setting. This is simple enough if you are confident with DIY (see https://www.diydata.com/problem/immersion/immersion_adjustment.php).
| Standard Operation |  |  | Weekly Legionella cycle |  |  |  | Notes
| Low | Medium | High | Low | Medium | High
Initial cylinder temperature | 65 | 70 | 75 | 65 | 70 | 75 | °C | CAR expert opinion
Final cylinder temperature | 60 | 60 | 60 | 51.5 | 51.5 | 51.5 | °C | This is an average of 50°C most days and 60°C once a week. However, controls do not usually have this flexibility.
Mean room temperature | 18 | 18 | 18 | 18 | 18 | 18 | °C
Distribution and storage losses (system boilers) | 700 | 1000 | 1500 | 700 | 1000 | 1500 | kWh/year | CHM modelling - gas and oil boilers are similar
CHM calculations reference temperature | 70 | 70 | 70 | 70 | 70 | 70 | °C
Initial losses | 632.6923 | 1000 | 1644.2308 | 632.6923 | 1000 | 1644.2308 | kWh/year | Assume losses are directly proportional the temperature difference between the cylinder and the room.
Reduced DHW temp losses | 565.3846 | 807.6923 | 1211.5385 | 450.9615 | 644.2308 | 966.3462 | kWh/year
Savings | 67.3077 | 192.3077 | 432.6923 | 181.7308 | 355.7692 | 677.8846 | kWh/year
Gas boiler efficiency for hot water - high efficiency means low savings | 74% | 70% | 64% | 74% | 70% | 64% |  | SAP10.2 | Summer efficiency for system boilers
Gas boiler efficiency for space heating | 85% | 80% | 75% | 85% | 80% | 75% |  | SAP10.2 | Winter efficiency for system boilers
Proportion of losses that are useful gains | 90% | 80% | 50% | 90% | 80% | 50% |  | Same as combi keep hot
Gas saved from water heating | 90.9563 | 274.7253 | 676.0817 | 245.5821 | 508.2418 | 1059.1947 | kWh/year
Additional gas use for space heating | 7.9186 | 48.0769 | 288.4615 | 21.3801 | 88.9423 | 451.9231 | kWh/year
Net gas savings | 83.0378 | 226.6484 | 387.6202 | 224.202 | 419.2995 | 607.2716 | kWh/year
Oil boiler efficiency (water heating) | 72% | 69% | 66% | 72% | 69% | 66% |  | SAP10.2 | Summer efficiency for system boilers
Oil boiler efficiency (space heating) | 84% | 81% | 78% | 84% | 81% | 78% |  | SAP10.2 | Winter efficiency for system boilers
Oil saved from water heating | 93.4829 | 278.7068 | 655.5944 | 252.4038 | 515.6076 | 1027.0979 | kWh/year
Additional oil use for space heating | 8.0128 | 47.4834 | 277.3669 | 21.6346 | 87.8443 | 434.5414 | kWh/year
Net oil savings | 85.4701 | 231.2234 | 378.2275 | 230.7692 | 427.7633 | 592.5565 | kWh/year
Potential uptake | Low | Medium | High
Proportion of gas boilers that are system boilers | 30.4% | 32% | 35.2% |  | Add uncertainy bands to account for scaling from England to the UK
Proportion of oil boilers that are system boilers | 74.1% | 78% | 85.8% |  | Add uncertainy bands to account for scaling from England to the UK
Proportion of households with a system boiler who can turn down the cylinder temperature without running out of hot water | 50% | 80% | 95% |  | CAR expert opinion
Proportion of all UK households (gas) | 12.7% | 21.39% | 27.94%
Proportion of all UK households (oil) | 1.987% | 3.347% | 4.372%
Total | 14.69% | 24.74% | 32.31%
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Reducing the cylinder temperature to 60°C | 83.0378 | 226.6484 | 387.6202 | 230.7692 | 427.7633 | 592.5565 | 0 | 0 | 0 | 3575.8367 | 6022.4618 | 7866.8408 | 559.5298 | 942.366 | 1230.9656 | 0 | 0 | 0 | -
Reduce the cylinder temperature to 50°C with a weekly Legionella cycle | 224.202 | 419.2995 | 607.2716 | 230.7692 | 427.7633 | 592.5565 | 0 | 0 | 0 | 3575.8367 | 6022.4618 | 7866.8408 | 559.5298 | 942.366 | 1230.9656 | 0 | 0 | 0 | -

## Reducing DHW temp. (combi)
Reduce the hot water temperature setting on your combi boiler
This measure applies to homes with a combi boiler
If you have a combi boiler you can control the temperature at which it supplies hot water to your taps and showers.
Reducing the temperature at which hot water is supplied can make energy savings because it takes less fuel to heat the water. SAP10.2 assumes that hot water for taps is supplied at 52°C and showers at 41°C.
However, when we use a shower or fill a bath, householders mix in sufficient water to get a comfortable temperature. If we reduce the temperature for hot water householders simply add less cold and the same amount of heat overall is used.
The distribution loss is the heat lost from pipes that deliver water to taps, when no water is flowing. SAP assumes this is 15% of the supplied water. However, we model this as half that because in the heating season those losses are useful gains, which will have to be replaced by space heating.
Water use calculations from SAP Appendix J | Low | Medium | High
Hot water temp (initial) | 50 | 52 | 55 | °C | SAP assumes the hot water supply is at 52°C and showers are supplied at 41°C
Hot water temp (final) | 45 | 42 | 40 | °C
Cold water temp | 13 | 13 | 13 | °C | SAP calculates this monthly. This is an average.
Number of people | 2 | 2.5 | 3
Hot water consumption excluding showers and baths including distribution loss | 36.12 | 41.3875 | 46.655 | litres/day | This calculation is from SAP. The distribution loss is 15% but we have halved that to allow for sone of the heat loss being useful gains that will have to be replaced by space heating.
Energy content (initial) | 566.3907 | 684.0698 | 830.4512 | kWh/year
Energy content (final) | 489.8514 | 508.6673 | 533.8615 | kWh/year
Savings | 76.5393 | 175.4025 | 296.5897 | kWh/year
Other assumptions | Low | Medium | High
Gas water heating efficiency | 74% | 70% | 64% |  | High efficiency reduces savings
Oil water heating effiiciency | 72% | 69% | 66% |  | High efficiency reduces savings
Bill savings per household (kWh or £) |  | kWh/year |  |  | £/year
|  | Low | Medium | High | Low | Medium | High
Reduce DHW temperature | Gas | 103.4315 | 250.575 | 463.4214 | 11 | 26 | 48
| Oil | 106.3046 | 254.2066 | 449.3784 | 10 | 25 | 43
Potential uptake |  | Low | Medium | High
Proportion of homes with a gas combi boiler | Gas | 53.98% | 56.82% | 59.66%
Proportion of homes with an oil combi boiler | Oil | 1.121% | 1.18% | 1.239%
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Reduce DHW temperature to 45°C (low savings), 42°C, or 40°C (high savings) | 103.4315 | 250.575 | 463.4214 | 106.3046 | 254.2066 | 449.3784 | 0 | 0 | 0 | 15197.3061 | 15997.1643 | 16797.0225 | 315.6322 | 332.2444 | 348.8566 | 0 | 0 | 0 | -

## Moving furniture
Moving furniture away from radiators
This measure could apply to most homes with wet heating systems.
When a radiator is obstructed by furniture it is less effective at transferring heat into the room. Radiators transfer heat by a combination of radiation and convection. The obstruction restricts convection, because this relies on free air flow. This means a higher proportion of the transfer is by convection. Radiant transfer is also intercepted by the obstruction, which warms as a result. This heat is ultimately transferred into the room but it takes longer to get there.
The obstructed radiators give lower thermal comfort too, because there is less radiant heat falling on the occupants.
We adapted the CODE model to examine the effects of adding obstacles in front of a radiator. We introduced radiator obstructions by reducing the capacity of the radiator and by increasing the radiative component in step. Initially, radiators transfer 30% by radiation and 70% by convection. The capacity reduction is taken from the convection only, so when capacity is reduced by 20% we increase the radiatiant fraction from 30% to 37.5%.
When an obstacle is removed, the radiator becomes more efficient and heats the room more quickly. This uses more energy rather than less. Also, the radiant heat absorbed by an obstruction it continues to heat the room when the heating is off. This uses more energy and when the obstruction is removed the effect reverses, giving savings. For small obstacles, the stored radiant heat has the greater effect and gas consumption increases, but the effect is small. With significant obstacles, the increased capacity wins out and heating energy demand increases.
There are two other potential effects from the clearing obstructions from the radiators. These are indirect and require additional behaviours. It is possible that the household has turned up the thermostat in an attempt to offset the problem with heating. If this is the case, they could turn down the thermostat a little, which will save energy. In addition, it is possible that improvement in radiator efficiency could enable turning down the flow temperature, with improvement in boiler efficiency. We have not included these effects in the modelling here.
Overall, our modelling indicates that there are no significant heat savings from removing obstructions from radiators and if anything heating demand is likely to increase.
Modelling with 12 CODE archetypes |  | Savings (%)
| Reduction in capacity | median | lower quartile | upper quartile | weighted mean
| 10% | 0% | 0.2% | -0.1% | 0%
| 20% | 0% | 0.3% | -0.2% | 0%
For this case we excluded one archetype where the effect of the obstruction was so great it did not heat the house effectively. | 40% | -0.7% | -0.1% | -1.3% | -0.9%
Impact of furniture on radiator heating capacity | Low | Medium | High
According to CIBSE a radiator in a cabinet with a grill at the front has 30% less heating emissions. This is our medium case - perhaps equivalent to a radiator half blocked by armchairs. The high case could be a radiator largely obstructed by a sofa and the low case, a radiator with a table in front. | 10% | 30% | 50% | CAR expert opinion as described, left
Proportion of radiators impacted per house | 20% | 40% | 80% | CAR expert opinion as described, left
Overall impact on radiator capacity in affected homes | 2% | 12% | 40%
Impact of furniture on gas use in affected homes, for gas heated homes - from the modelling above | -0.1% | 0% | -1.3%

## Closing curtains
Closing curtains at night
This measure could apply to all homes who do not already close curtains at night.
SAP 10.2 assumes that all windows have curtains and curtains are closed for half the time. They assume curtains have an effective resistance of 0.04 m2K/W (based on. 0.08 m2K/W for half the time, i.e. 12/24 hours).
We have used the Cambridge Housing Model, which is based on SAP and has the same curtain resistance factor, to test the annual saving by area and type of window.
In practice, the savings vary considerably depending on the curtain and other factors. Savings are greatest for a single-glazed window above a radiator and the curtains are tucked behind it (up to 30%). Savings are lower for double-glazed windows, or where there is no radiator, or where the curtain is not well fitted into the reveal so that air can move freely around it. [Salford]
Our approach starts with using the CHM to estimate the annual energy savings by area of window, single or double and by fuel type. The CHM was run with and without the closed curtains assumption. Differences by fuel are mainly to do with efficiency. We then scale up to a household using the average area of windows and the average proportion of single and double glazing.
Closing curtains at night improves thermal comfort because it increases the radiative temperature in the room, by hiding the cold glass surface, and it also reduces draughts in the vicinity of the window
In this table and chart, low and high levels are the 25% and 75% quantiles for savings across the stock.
Savings (modelled in the CHM) by window area | Gas low | Gas Mean | Gas high | Oil low | Oil Mean | Oil high | Elec low | Elec Mean | Elec high
Closing curtains on single glazed windows | 28 | 34 | 37 | 26 | 30 | 33 | 32 | 33 | 34 | kWh/m2/year
Closing curtains on double glazed windows | 14 | 16 | 18 | 13 | 15 | 16 | 14 | 15 | 17 | kWh/m2/year
Dwelling factors by fuel (data from the CHM) | Gas |  |  | Oil |  |  | Electricity
Typical area of windows (m2) | 18 |  |  | 31 |  |  | 11 |  |  | m2
Proportion of windows that are single glazed | 8% |  |  | 18% |  |  | 12%
Proportion of windows where curtains are not closed | Low | Medium | High
Proportion of windows where curtains are currently left open, in homes which do not already close curtains for all windows. | 10% | 30% | 50% | CAR expert opinion
Typical household bill savings , based on the typical area of windows | Gas |  |  | Oil |  |  | Electricity
Proportion of UK homes | 83.56% |  |  | 5.364% |  |  | 7.617%
| Low | Medium | High | Low | Medium | High | Low | Medium | High
single glazing | 4.032 | 14.688 | 26.64 | 14.508 | 50.22 | 92.07 | 4.224 | 13.068 | 22.44 | kWh/year
double glazing | 23.184 | 79.488 | 149.04 | 33.046 | 114.39 | 203.36 | 13.552 | 43.56 | 82.28 | kWh/year
Total kWh | 27.216 | 94.176 | 175.68 | 47.554 | 164.61 | 295.43 | 17.776 | 56.628 | 104.72 | kWh/year
Total £/year | 2.8032 | 9.7001 | 18.095 | 4.5946 | 15.9043 | 28.544 | 6.0438 | 19.2535 | 35.6048 | £/year
Potential uptake | Low | Medium | High
Proportion of homes where some windows do not have closed curtains at night | 40% | 50% | 60% | According to [ONSwellbeing], 51% of adults said they closed all the curtains at night to keep the heat in, but this is not precise.
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Closing curtains at night | 27.216 | 94.176 | 175.68 | 47.554 | 164.61 | 295.43 | 17.776 | 56.628 | 104.72 | 9410.0966 | 11762.6208 | 14115.1449 | 604.0808 | 755.1009 | 906.1211 | 857.8357 | 1072.2946 | 1286.7535 | -
The CHM model assumed a curtain resistance of 0.04, based on a resistance of 0.08 half the time. Here we calculate the corrsponding savings to compare with the literature below.
Curtains - thermal resistance | 0.08
Impact on double glazing |  | U-value | Resistance | Add curtains | Resulting U-value | Heat savings
| Double glazing U-value | 2 | 0.5 | 0.58 | 1.7241 | 13.79%
| Single glazing U-value | 4.6 | 0.21739 | 0.29739 | 3.3626 | 26.9%
| Secondary glazing | 2.8 | 0.35714 | 0.43714 | 2.2876 | 18.3%
Literature review
Historic England | Heavy curtains mounted outside the reveal
|  | U-value | R-value | Resistance of covering | %age savings
Table 1 black window | Single glazing | 5.2 | 0.19231
| + curtains | 3 | 0.33333 | 0.14103 | 42.31%
Table 2 | Secondary glazing | 2.8 | 0.35714
| + curtains | 1.9 | 0.52632 | 0.16917 | 32.14%
| + honeycomb blind in reveal | 1.8 | 0.55556 | 0.19841 | 35.71%
| + honeycomb blind outside reveal | 2.2 | 0.45455 | 0.097403 | 21.43%
Salford test on sash windows with single glazing | Lined curtains | Savings (%) | Initial U-value | Final U-value | Resistance
Living room | Curtain tucked behind radiator | 27.8 | 5.1 | 3.6822 | 0.075498
Kitchen | Roller blind, bottom on window (no rad) | 12.3 | 4.32 | 3.7886 | 0.032465
Bedroom 1 | Lined curtain drapes below sill | 4.9 | 4.5 | 4.2795 | 0.01145
Bedroom 2 | Lined curtain drapes below sill | 10.3 | 4.45 | 3.9917 | 0.025804
Bathroom | Roller blind bottom on windowsill (above rad) | 29.1 | 4.43 | 3.1409 | 0.092649

## Window treatments
Treating windows with film
This measure could apply to almost all homes.
Window film is a form of temporary secondary glazing. It has two effects: reducing draughts and reducing conductive heat loss through the glass. Research suggests savings of 25% on heat loss through the centre of the pane. However, there are very few studies on this.
The impact of draught fixing is minor, averaged over the stock. However, the effect of reducing heat loss through windows is considerable, because windows lose a lot of heat: up to 10 times as much per m2 as walls.
For the conductive heat losses we used the figure of 25% reduction in conductive heat loss, based on the study of StormGuard secondary glazing film by R Fitton (2014). (Note that other brands are available, and these likely have similar performance.) Savings can be higher, in the case of windows that were draughty, or lower because of poor installation.
The modelling approach starts by using the CHM to model savings per unit area of window. We reduced draughts through doors and windows by half and we added thermal resistance to each of 0.07 m2K/W - equivalent to a 25% reduction in heat flow for a single-glazed window with timber frames. The savings vary considerably depending on the type of window- much more for single glazing than double glazing - so we keep these calculations separate. This is then scaled to household level assuming a typical area of window of each type. Electrically heated homes tend to be smaller and have fewer windows, oil heated homes are larger with more windows, and a higher proportion of single-glazed windows.
In this table (and the chart), low and high levels are the 25% and 75% quantiles for savings across the stock.
Savings (modelled in the CHM) by window area | Gas low | Gas Mean | Gas high | Oil low | Oil Mean | Oil high | Elec low | Elec Mean | Elec high
Film on single-glazed windows | 38 | 50 | 52 | 35 | 42 | 45 | 36 | 46 | 48 | kWh/m2/year
Film on double-glazed windows | 18 | 21 | 23 | 17 | 19 | 21 | 18 | 19 | 22 | kWh/m2/year
Dwelling factors by fuel (data from the CHM) | Gas | Oil | Electricity
Typical area of windows (m2) | 18 | 31 | 11 | m2
Proportion of windows that are single glazed | 8% | 18% | 12%
Modifying household factors | Low | Medium | High
Factor for savings per unit area - depending on installation quality and initial draughtiness of windows | 0.7 | 0.9 | 1.1 |  | CAR expert opinion
Typical household bill savings, based on the typical area of windows | Gas |  |  | Oil |  |  | Electricity
Proportion of homes | 83.56% |  |  | 5.364% |  |  | 7.617%
| Low | Medium | High | Low | Medium | High | Low | Medium | High
Single glazing | 38.304 | 64.8 | 82.368 | 136.71 | 210.924 | 276.21 | 33.264 | 54.648 | 69.696 | kWh/year
Double glazing | 208.656 | 312.984 | 418.968 | 302.498 | 434.682 | 587.202 | 121.968 | 165.528 | 234.256 | kWh/year
Total kWh | 246.96 | 377.784 | 501.336 | 439.208 | 645.606 | 863.412 | 155.232 | 220.176 | 303.952 | kWh/year
Total £/year | 25.4369 | 38.9118 | 51.6376 | 42.4356 | 62.3774 | 83.4214 | 52.7789 | 74.8598 | 103.3437 | £/year
Potential Uptake | Low | Medium | High
In some cases there is not enough space between the window and the frame surface to install window film. | 80% | 90% | 100% |  | CAR expert opinion
Number of participating households | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High
Number of homes | 18820193.264 | 21172717.422 | 23525241.58 | 1208161.52 | 1359181.71 | 1510201.9 | 1715671.312 | 1930130.226 | 2144589.14
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Add window film to all windows | 246.96 | 377.784 | 501.336 | 439.208 | 645.606 | 863.412 | 155.232 | 220.176 | 303.952 | 18820.1933 | 21172.7174 | 23525.2416 | 1208.1615 | 1359.1817 | 1510.2019 | 1715.6713 | 1930.1302 | 2144.5891 | low
Add window film to all single glazed windows | 38.304 | 64.8 | 82.368 | 136.71 | 210.924 | 276.21 | 33.264 | 54.648 | 69.696 | 18820.1933 | 21172.7174 | 23525.2416 | 1208.1615 | 1359.1817 | 1510.2019 | 1715.6713 | 1930.1302 | 2144.5891 | low

## Loft insulation
Installing or topping up loft insulation
This measure could apply to almost all homes that have a pitched roof not converted to an attic.
Most homes have some loft insulation already but there are around 265,000 that do not. There are diminishing returns to adding more top-up insulation, but it is still worth doing in many cases. The shape and size of the dwelling matters: this is more important for homes with a large area of roof.
Adding loft insulation improves thermal comfort in the rooms below the roof. It can help keep rooms cool in summer as well as retaining heat in winter. It can also alleviate problems with cold spots and mould on ceilings.
Loft insulation is hard to add in homes where there is a room in roof or a flat roof. We only consider pitched roofs without a room in roof. Also, where homes have upper rooms with sloping ceilings that are part of the roof, it may not be possible to insulate these areas without blocking ventilation to roof timbers. Ignoring this can lead to condensation and mould.
The modelling approach starts with using the CHM to model savings from adding to the existing loft insulation, per unit area of roof. We modelled the savings starting with six different levels of insulation and topping up to 300mm. The benefits are very large if you start with none, but they dimininish rapidly. The savings for oil-heated homes are very similar to gas homes with the same level of insulation. For electrically heated homes, the differences are a little greater, mainly due to different heating efficiency. We also used data from the CHM to determine the proportion of the stock with different levels of insulation. These proportions vary little with different fuel types.
National statistics on energy savings from (top-up) loft insulation (NEED) report a mean 3% saving for loft insulation (approx. £30/year), with a median of 4%. This is a little less than our estimate for a top-up from 100-150mm to 300mm. However, savings can be much higher for homes starting with less insulation.
The number of homes in the table below reflects the number of homes in the CHM dataset, which represent homes in England only. This is scaled to UK in Rows 45 to 52. We modelled only homes with a pitched roof and no room in roof, and homes with inaccessible lofts were excluded.
CHM Modelling results, savings/roof area (kWh/m2) | Gas |  |  |  |  | Electric |  |  |  |  | Oil |  | Gas
| Number of homes | Mean roof area | Low | Medium | High | Number of homes | Mean roof area | Low | Medium | High | Number of homes | Mean roof area | Bill savings %age
None to 300mm | 224576.95 | 53 | 83 | 95.2 | 105.8 | 18483.32 | 47.9 | 70.3 | 79.6 | 89.9 | 21989.49 | 66 | 28%
0- 50, to 300mm | 754335.33 | 50 | 22.5 | 27.7 | 31.3 | 72639.43 | 51.1 | 21.6 | 23.8 | 25.6 | 35926.21 | 89 | 11%
50-100 to 300mm | 3768232.53 | 52.51 | 10 | 13.1 | 14.7 | 171863.06 | 43.6 | 9.4 | 10.9 | 12.1 | 175835.07 | 94 | 5.8%
100-150 to 300mm | 3164104.44 | 51.8 | 6.8 | 8 | 9 | 182021.82 | 51.8 | 6.2 | 6.9 | 7.8 | 151126.68 | 80.4 | 3.8%
150-200 to 300mm | 2762323.83 | 49.8 | 2.9 | 3.3 | 3.7 | 151166.45 | 48.6 | 2.6 | 2.9 | 3.3 | 112846.89 | 89.3 | 1.6%
200-250 to 300mm | 2665424.05 | 50.7 | 1.3 | 1.4 | 1.6 | 144042.72 | 45.3 | 1.1 | 1.2 | 1.4 | 89915.77 | 86.6 | 0.7%
More than 300mm | 2474442.88 | 51.6 |  |  |  | 125777.2 | 52.7 |  |  |  | 106033.9 | 79.8
Electrically heated homes tend to be smaller and oil heated homes larger. For calculating household savings we use a typical roof size, which is different for each fuel - based on the data in the CHM.
Roof area | Gas | Oil | Electric
Mean roof area | 54.4 | 87.9 | 50.6
Householder savings from upgrading loft insulation kWh/year | Gas |  |  | UK proportion of homes | Oil |  |  | UK proportion of homes | Electricity |  |  | UK proportion of homes | UK Total proportion of homes |  |  | Normalised
| Low | Medium | High |  | Low | Medium | High |  | Low | Medium | High |  |  |  |  | Gas | Oil | Electricity
None to 300mm | 4515.2 | 5178.88 | 5755.52 | 0.9285% | 7295.7 | 8368.08 | 9299.82 | 0.1673% | 3557.18 | 4027.76 | 4548.94 | 0.08096% | 1.177% |  | None | 1.42% | 3.17% | 2.134%
0- 50, to 300mm | 1224 | 1506.88 | 1702.72 | 3.119% | 1977.75 | 2434.83 | 2751.27 | 0.2734% | 1092.96 | 1204.28 | 1295.36 | 0.3182% | 3.71% |  | 1 to 50mm | 4.77% | 5.179% | 8.388%
50-100 to 300mm | 544 | 712.64 | 799.68 | 15.58% | 879 | 1151.49 | 1292.13 | 1.338% | 475.64 | 551.54 | 612.26 | 0.7528% | 17.67% |  | 51-100mm | 23.83% | 25.35% | 19.85%
100-150 to 300mm | 369.92 | 435.2 | 489.6 | 13.08% | 597.72 | 703.2 | 791.1 | 1.15% | 313.72 | 349.14 | 394.68 | 0.7973% | 15.03% |  | 101-150mm | 20.01% | 21.79% | 21.02%
150-200 to 300mm | 157.76 | 179.52 | 201.28 | 11.42% | 254.91 | 290.07 | 325.23 | 0.8586% | 131.56 | 146.74 | 166.98 | 0.6622% | 12.94% |  | 151-200mm | 17.47% | 16.27% | 17.46%
200-250 to 300mm | 70.72 | 76.16 | 87.04 | 11.02% | 114.27 | 123.06 | 140.64 | 0.6841% | 55.66 | 60.72 | 70.84 | 0.631% | 12.34% |  | 201-250mm | 16.86% | 12.96% | 16.63%
[15 empty] | 251-350mm | 15.65% | 15.29% | 14.52%
Homes with inaccessible lofts | Low | Medium | High
| 10% | 5% | 1% | CAR expert opinion
Proportion of homes that can upgrade loft insulation | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High
None to 300mm | 0.8357% | 0.8821% | 0.9192% | 0.1506% | 0.1589% | 0.1656% | 0.07287% | 0.07691% | 0.08015%
0- 50, to 300mm | 2.807% | 2.963% | 3.088% | 0.246% | 0.2597% | 0.2706% | 0.2864% | 0.3023% | 0.315%
50-100 to 300mm | 14.02% | 14.8% | 15.42% | 1.204% | 1.271% | 1.324% | 0.6775% | 0.7152% | 0.7453%
100-150 to 300mm | 11.77% | 12.43% | 12.95% | 1.035% | 1.092% | 1.138% | 0.7176% | 0.7575% | 0.7893%
150-200 to 300mm | 10.28% | 10.85% | 11.31% | 0.7728% | 0.8157% | 0.85% | 0.5959% | 0.6291% | 0.6555%
200-250 to 300mm | 9.918% | 10.47% | 10.91% | 0.6157% | 0.6499% | 0.6773% | 0.5679% | 0.5994% | 0.6246%
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
None to 300mm | 4515.2 | 5178.88 | 5755.52 | 7295.7 | 8368.08 | 9299.82 | 3557.18 | 4027.76 | 4548.94 | 235.2748 | 248.3457 | 258.8023 | 42.3939 | 44.7491 | 46.6333 | 20.5148 | 21.6545 | 22.5663 | high
0- 50, to 300mm | 1224 | 1506.88 | 1702.72 | 1977.75 | 2434.83 | 2751.27 | 1092.96 | 1204.28 | 1295.36 | 790.2686 | 834.1724 | 869.2955 | 69.2628 | 73.1107 | 76.189 | 80.6231 | 85.1022 | 88.6854 | high
50-100 to 300mm | 544 | 712.64 | 799.68 | 879 | 1151.49 | 1292.13 | 475.64 | 551.54 | 612.26 | 3947.7349 | 4167.0535 | 4342.5084 | 338.9955 | 357.8286 | 372.895 | 190.7522 | 201.3496 | 209.8274 | medium
100-150 to 300mm | 369.92 | 435.2 | 489.6 | 597.72 | 703.2 | 791.1 | 313.72 | 349.14 | 394.68 | 3314.8288 | 3498.9859 | 3646.3116 | 291.3597 | 307.5464 | 320.4957 | 202.0275 | 213.2512 | 222.2302 | medium
150-200 to 300mm | 157.76 | 179.52 | 201.28 | 254.91 | 290.07 | 325.23 | 131.56 | 146.74 | 166.98 | 2893.909 | 3054.6818 | 3183.3 | 217.5595 | 229.6461 | 239.3154 | 167.7809 | 177.102 | 184.559 | low
200-250 to 300mm | 70.72 | 76.16 | 87.04 | 114.27 | 123.06 | 140.64 | 55.66 | 60.72 | 70.84 | 2792.3934 | 2947.5263 | 3071.6327 | 173.3502 | 182.9807 | 190.6852 | 159.8742 | 168.7561 | 175.8616 | low

## Radiator foil
Fitting foil behind radiators on external walls
This measure could apply to almost all homes with wet heating systems.
When a radiator on an external wall heats up it heats up the wall as well as the room. The wall becomes warmer than adjacent sections and there is higher heat loss. This is often seen in infrared images of homes, especially those with uninsulated solid walls. The heat loss can be reduced by installing a thin reflective panel into the spacel behind the radiator. This can even by a piece of cardboard covered with ordinary kitchen foil. The foil helps to reflect the heat back into the room rather than heating up the wall.
There is very limited evidence however. A report evaluating a product called Radflek (for radiator reflector) shows heat loss through the wall reduced by nearly half. There are errors in calculations in the report, but we were able to use the raw data and avoid the errors.
Heat transfer to the wall at that distance will be mainly from radiation rather than convection and determined by the temperature of the radiator. Thus we can expect similar savings for different types of radiator, depending only on the surface temperature. There are bigger savings from walls with higher conductive losses.
Our approach for modelling this is first to use the test results to estimate heat savings by area of radiator against the wall. This is different depending oon the type of wall. Then we use this to estimate the fraction of space heating lost (depending on the proportion of radiators against external walls, and the heat output of the radiator relative to the heat losses).
This measure only applies to wet heating systems, so homes using gas or oil for heating.
Radflek test results
The tests were conducted on two walls, one with U-value 1.1 W/m2K. and a second one with U-value 2.1. The tests measured temperature at the surface of the radiator and the inner and outer surfaces of the wall as as well as the cold box surrounding the test setup. | [6 empty] | We have plotted the results from the analysis (left) in the chart below.
Then used interpolation from the chart to estimate savings from different types of wall.
Test measurements - from Radflek
| wall1 |  | wall2
U-value | 1.1 | 1.1 | 2.1 | 2.1 | W/m2K
| No sheet | with sheet | No sheet | with sheet
rad temp | 50.7 | 50.7 | 51.5 | 50.8 | K
inner wall | 34.5 | 19.9 | 29 | 15.9 | K
outer wall | 1.8 | 2.2 | 3.8 | 2.4 | K
cold box | 0.2 | 1 | 0.2 | 0.5 | K
Heat flow analysis
Temp diff across wall | 32.7 | 17.7 | 25.2 | 13.5 | K
U-value adjusted for surface resistance | 0.97 | 0.97 | 1.97 | 1.97 | W/m2K
Heat flow | 31.719 | 17.169 | 49.644 | 26.595 | W/m2
Heat saving from the sheet |  | 14.55 |  | 23.049 | W/m2
Effective U-value between the radiator and the wall - this assumes that heat transfer is linear depending on the radiator surface temperature and the outside temperature | 0.6281 | 0.34545 | 0.96772 | 0.52873 | W/m2K
[7 empty] | U-value | Savings (W/m2)
Adustment for mean winter conditions | [6 empty] | 0 | 0
Tdiff for 50-rad to 5-ext | 45 | 45 | 45 | 45 | K |  | 1.1 | 15.5455
Heat flow | 28.2645 | 15.5454 | 43.5474 | 23.7927 | W/m2 |  | 2.1 | 24.1445
Heat saving from the sheet |  | 12.7191 |  | 19.7546 | W/m2
Adjustment for higher radiator temperature 60C
Tdiff for 60-rad to 5-ext | 55 | 55 | 55 | 55 | K
Heat flow | 34.5454 | 18.9999 | 53.2246 | 29.08 | W/m2
Heat saving from the sheet |  | 15.5455 |  | 24.1445 | W/m2
Based on the data on external wall U-values in the CHM (see chart) we have chosen three typical U-values and classified the dwellings into three groups according to which they are closest to.
The savings for these U-values have been calculated by interpolating from the results above.
| U-value | Savings (W/m2) | Proportion of homes
Modern cavity walls - low U-values up to 0.5 | 0.35 | 5.6381 | 16.6% | CHM
Retrofit filled cavity - 0.5 to 1.0 | 0.65 | 9.9569 | 40.7% | CHM
Solid or unfilled cavity - 1.5 to 2.5 | 1.6 | 20.5043 | 42.7% | CHM
Savings as a proportion of household bill - depends on radiator type | Low | Medium | High
Radiator output W/m2 | 3000 | 1500 | 1000 | CAR expert opinion
Type of wall
As-built insulated cavity walls | 0.1879% | 0.3759% | 0.5638% | %age of space heating
Retrofit filled cavity | 0.3319% | 0.6638% | 0.9957% | %age of space heating
Solid or unfilled cavity | 0.6835% | 1.367% | 2.05% | %age of space heating
Other household factors | Low | Medium | High
Proportion of radiators on external walls | 50% | 80% | 90% | CAR expert opinion - radiators are often positioned below windows in which case they are always on external walls
Proportion of radiators with inaccessible spaces | 10% | 5% | 2% | CAR expert opinion - rads may be enclosed or awkwards positioned below projecting windows sills
Uncertainy in savings from sheet | 80% | 100% | 120% | CAR expert opinion
All household factors | 36% | 76% | 105.8%
Typical household savings from installing foil sheet (kWh/year) | Gas |  |  | Oil
| low | medium | high | low | medium | high
Modern cavity wall | 6.4727 | 27.3291 | 57.089 | 10.8309 | 45.7306 | 95.5288
retrofit filled cavity | 11.4308 | 48.2634 | 100.8198 | 19.1276 | 80.7608 | 168.705
Solid or unfilled cavity | 23.5395 | 99.3889 | 207.6182 | 39.3894 | 166.3107 | 347.4143
Typical household savings from installing foil sheet (£/year) | Gas |  |  | Oil
| low | medium | high | low | medium | high
Modern cavity wall | 0.66669 | 2.8149 | 5.8802 | 1.0465 | 4.4184 | 9.2298
Retrofit filled cavity | 1.1774 | 4.9711 | 10.3844 | 1.8481 | 7.803 | 16.3
Solid or unfilled cavity | 2.4246 | 10.2371 | 21.3847 | 3.8057 | 16.0687 | 33.5666
Potential uptake | Gas |  |  | Oil |  |  | Total
UK proportion of homes with… | low | medium | high | low | medium | high | low | medium | high
Modern cavity wall | 12.48% | 13.87% | 15.26% | 0.7124% | 0.8904% | 0.9795% | 13.2% | 14.76% | 16.24% | Low/high bands reflect uncertainty in scaling from England to the UK
Retrofit filled cavity | 27.21% | 34.01% | 37.41% | 1.747% | 2.183% | 2.402% | 28.95% | 36.19% | 39.81% | Low/high bands reflect uncertainty in scaling from England to the UK
Solid or unfilled cavity | 28.54% | 35.68% | 39.25% | 1.832% | 2.29% | 2.52% | 30.38% | 37.97% | 41.77% | Low/high bands reflect uncertainty in scaling from England to the UK
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Modern cavity wall | 6.4727 | 27.3291 | 57.089 | 10.8309 | 45.7306 | 95.5288 | 0 | 0 | 0 | 3514.6711 | 3905.1901 | 4295.7091 | 200.5548 | 250.6935 | 275.7629 | 0 | 0 | 0 | -
retrofit filled cavity | 11.4308 | 48.2634 | 100.8198 | 19.1276 | 80.7608 | 168.705 | 0 | 0 | 0 | 7659.8187 | 9574.7733 | 10532.2507 | 491.7217 | 614.6522 | 676.1174 | 0 | 0 | 0 | -
Solid or unfilled cavity | 23.5395 | 99.3889 | 207.6182 | 39.3894 | 166.3107 | 347.4143 | 0 | 0 | 0 | 8036.2225 | 10045.2782 | 11049.806 | 515.885 | 644.8562 | 709.3418 | 0 | 0 | 0 | -

## Smart thermostats & compens'n
Install a smart thermostat, one with load compensation, or weather-compensating controls.
This measure could apply to all homes with modulating boilers that are compatible with OpenTherm
Load compensation and weather compensation work with modulating boilers to adjust the power output according to either heating demand in rooms ('load compensation'), or the outdoor temperature ('weather compensation'). Lower power generally means a lower flow temperature, which also means a lower return temperature - so the boiler runs in condensing mode more of the time. However, the temperature difference between flow and return also reduces unless the boiler has an integrated circulation pump and lowers the speed as well.
Load-compensating controllers adjust the power output according to the difference between the internal temperature and the target temperature. If the internal temperature is too low, the power is increased, and vice versa.
Weather-compensating controllers adjust the power output according to the temperature outside. They use either a physical sensor, or temperature information from sources on the internet . When it is cold the power output is increased and vice versa. The relationship is set by a curve which can be adjusted up or down, depending on the dwelling heat losses. Getting this right requires either careful calculation or experiment. In University of Salford tests [SalfordTherm] -the weather compensating controls failed to heat rooms adequately until the heating system was optimised by balancing the radiators, range rating the boiler, and setting an appropriate pump speed.
When they are set correctly, weather compensating controls give a slower response than load-compensating controls. This makes them less suited to intermittent heating (but good for heat pumps).
Intelligent thermostats such as NEST can automatically adjust heating schedules and set-point temperatures according to the requirements of the occupants. Most systems use presence sensors to do this.
SAP reports higher savings from load-compensating controls in oil boilers compared to gas, but the opposite for weather compensation. However, the product characteristics database lists only two modulating controllers for oil boilers - both Class VIII, which is a combination of load compensation with zone controls. Also multiple sources report that most oil boilers cannot modulate, so very few installed systems would be able to benefit. Further, few oil boilers support OpenTherm. Overall the potential uptake for modulating controls on oil boilers is not significant.
Efficiency savings for different types of controls, summary of data from all sources
|  | Class IV TPI | Class V Load | Class VI Weather | Smart (NEST) | Smart | Reference key
SAP 10.2 | Gas | 0% | 0.5% | 1.4% |  |  | SAP10 | These are the efficiency gains at 80/60 or 70/60 flow-return settings, so without reducing flow temperature
SAP 10.2 | Oil | 0% |  | 1.1% |  |  | SAP10 | Note Ofgem price caps do not specify difference between peak and non-peak rate
Salford - initial | Gas | 10% | 12% | - |  |  | SalfordTherm | Weather compensating controls failed to achieve comfort heating in the initial phase.
Salford - after tuning | Gas | 4% | 8% | 5% |  |  | SalfordTherm
BRE: Ecodesign regulations | Gas | 1% | 2% | 3% |  |  | BRE-controls | These are the efficiency improvemets relative to Class I
Behavioural Insights Team | Gas |  |  |  | 6.5% +/- 5% | 4.5% +/- 1.2% | NEST
Efficiency savings (gas and oil) | Low | Medium | High
Smart thermostat | 3% | 6.5% | 10% | CAR Expert opinion based on NEST study
Load compensation | 0.5% | 5% | 8% | CAR Expert opinion based on the range of different results
Weather compensation | 1.4% | 3% | 5% | CAR Expert opinion based on the range of different results
Bill savings per household (kWh or £) | kWh/year |  |  | £/year
| Low | Medium | High | Low | Medium | High
Smart thermostat | 287.0072 | 621.8488 | 956.6905 | 30 | 64 | 99
Load compensation | 47.8345 | 478.3453 | 765.3524 | 5 | 49 | 79
Weather compensation | 133.9367 | 287.0072 | 478.3453 | 14 | 30 | 49
Potential uptake
| Low | Medium | High
Proportion of boilers with modulation capability | 60% | 75% | 85% | CAR expert opinion based on the list of Opentherm compatible boilers [Opentherm]
Proportion of homes that already have smart thermostats | 1% | 3% | 5% | CAR expert opinion
Proportion of homes with boilers that can install smart thermostat | 59% | 72% | 80%
Total proportion of homes | 49.3% | 60.16% | 66.85%
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Load compensation for boilers | 47.8345 | 478.3453 | 765.3524 | 0 | 0 | 0 | 0 | 0 | 0 | 13879.8925 | 16938.1739 | 18820.1933 | 0 | 0 | 0 | 0 | 0 | 0 | -
Weather compensation for boilers | 133.9367 | 287.0072 | 478.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 13879.8925 | 16938.1739 | 18820.1933 | 0 | 0 | 0 | 0 | 0 | 0 | -
Smart thermostats (e.g. NEST) | 287.0072 | 621.8488 | 956.6905 | 0 | 0 | 0 | 0 | 0 | 0 | 13879.8925 | 16938.1739 | 18820.1933 | 0 | 0 | 0 | 0 | 0 | 0 | low

## TRVs
Install TRVs on radiators
This measure could be applied to a) homes without TRVs, or b) homes with TRVs that are not fully utilised
Thermostatic Radiator Valves (TRVs) are now common in UK homes, but they are often left open - set to maximum temperature - and unused. This measure addresses the twin problems of a) TRVs not being installed in some homes and b) even when TRVs are installed on all radiators, they are commonly left at maximum settings. To achieve savings, TRVs should be adjusted according to household needs, with lower temperatures in bedrooms and other non-living areas. TRVs are modelled here as two separate measures - from no TRVs to with TRVs, and from TRVs on all radiators to correctly adjusted TRVs.
In SAP10, living areas are heated to 21°C and other areas are cooler, depending on the heat loss parameter and heating controls, and commonly 18 to 20°C. Low heat loss means a smaller difference betend to increase the difference. EFUS reports very similar average temperatures in the living room and bedrooms (0.5°C difference to main bedroom and 0.8°C difference to a third bedroom). This suggests that there is room for savings, although some households - such as those with a health problem - need warmer bedrooms.
Merely fitting TRVs makes no savings: it is the adjustment that matters, and precisely how TRVs are set up is ambiguous in SAP. This makes it difficult to generalise across the stock and there is very little field data.
We used two approaches to estimate savings. The first was based on modelling homes with and without TRVs using the CHM. We compared total gas use for homes that did have TRVs with the same homes without TRVs. Taken as a proportion of the bill, there was very little difference between gas boiler cases and oil boiler cases, so we used the same values for both.
The second approach used a study at the Salford Energy House (Timmins) which measured gas heating requirements at a range of external temperatures. It was not possible to achieve 18°C in the bedrooms because the heating could not modulate low enough, so the regime used was 24°C and 21°C. At a lower temperature the savings would be a little higher, because part of the heating energy is used for hot water, and this would not be affected by TRVs.
Reported results | Fuel | Mean | Low | High
CHM | Gas | 6.7% | 2.6% | 9.2%
CHM | Oil | 6.6% | 2.5% | 8.9%
Timmins - space heating only | Gas | 18% |  |  | This is based on tests at a range of external temperatures in a test house under controlled conditions, thermostat 24C and TRVs 21C.
Timmins - adjusted for the whole bill (reflecting DHW heating) |  | 14.68%
Efficiency savings (gas and oil) |  | Low | Medium | High
Installing TRVs and adjusting them. High savings assume 3°C lower bedrooms, bathrooms, kitchen and halls, as in Timmins. |  | 7% | 10.84% | 14.68% | Since the Timmins study was set for a 3°C difference and under 'lab conditions', e.g. with internal doors closed, we use this as the maximum saving. The low estimate reflects savings modelled in the CHM.
Adjusting TRVs that are already installed and partially adjusted, 1.5°C lower non-living rooms. |  | 0% | 5.419% | 10.84% | Assuming 'partial adjustment' achieves 1.5°C, and the new adjustment achieves another 1.5°C lower temperature in non-living rooms.
Bill savings per household (kWh or £) |  | kWh/year |  |  | £/year
|  | Low | Medium | High | Low | Medium | High
Installing TRVs (1.5°C cooler for Zone 2 outside the living room) | Gas | 821.3588 | 1271.7009 | 1722.043 | 85 | 131 | 177
| Oil | 1374.4066 | 2127.9788 | 2881.551 | 133 | 206 | 278
Readjusting TRVs (1.5°C cooler for Zone 2 outside the living room) | Gas | 0 | 635.8504 | 1271.7009 | 42.5 | 65.5 | 88.5
| Oil | 0 | 1063.9894 | 2127.9788 | 66.5 | 103 | 139
Potential uptake
|  | Low | Medium | High
Proportion of those homes with TRVs | all | 84% | 86% | 88% | For England from the CHM - with uncertainty bands
Proportion of homes without TRVs | Gas | 13.37% | 11.7% | 10.03% | If these homes do not currently set TRVs to achieve cooler non-living rooms
Proportion of homes without TRVs | Oil | 0.8583% | 0.751% | 0.6437%
Proportion of homes with TRVs | Gas | 70.19% | 71.86% | 73.53%
Proportion of homes with TRVs | Oil | 4.506% | 4.613% | 4.72%
Summary | Bill savings per participating household kWh/year | [8 empty] | Number of participating households (thousands) | [8 empty] | Comfort Improvement
| Gas |  |  | Oil |  |  | Electricity |  |  | Gas |  |  | Oil |  |  | Electricity
| Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
Starting from all rooms at the same temperature, adjust TRVs to 3°C cooler outside the living room | 821.3588 | 1271.7009 | 1722.043 | 1374.4066 | 2127.9788 | 2881.551 | 0 | 0 | 0 | 3764.0387 | 3293.5338 | 2823.029 | 241.6323 | 211.4283 | 181.2242 | 0 | 0 | 0 | -
Readjusting existing TRVs outside the living room to 1.5°C cooler than before | 0 | 635.8504 | 1271.7009 | 0 | 1063.9894 | 2127.9788 | 0 | 0 | 0 | 19761.2029 | 20231.7078 | 20702.2126 | 1268.5696 | 1298.7736 | 1328.9777 | 0 | 0 | 0 | -

## Assumptions
General assumptions
GHG emissions
kWh per tonne of oil equivalent (toe) | 11630 | kWh/toe
kWh per ktoe | 11630000
Gas GHG emissions (gross) | 0.184 | kg CO2e/kwh | GHGConv
| 184 | t CO2e/GWh
Electricity GHG emission | 0.194 | kg CO2e/kwh | GHGConv
Oil GHG emissions (gross) | 0.27 | kg CO2e/kwh | GHGConv
Energy prices
Price of gas | 10.3 | p/kWh
Price of electricity (standard) | 34 | p/kWh
Price of electricity (dual rate bill) | 34 | p/kWh | Note Ofgem price caps do not specify difference between peak and non-peak rate
Price of oil | 100 | p/litre | BoilerJuice
| 9.6618 | p/kWh
Demographics
Population of the UK (2020) | 67081234 |  | ONSPop
Population of England | 56550138 |  | ONSPop
Number of dwellings in the UK | 28153819
Population of Scotland | 5466000 |  | ONSPop
Population of Wales | 3169586 |  | ONSPop
Population of N, Ireland | 1895510
Gas heating
Total domestic sector gas use (UK) | 23735 | ktoe | ECUK | Table 3
Total domestic sector gas use (UK) | 276038050000 | kWh
Total gas for domestic space heating (UK) | 19352 |  | ECUK | Table 3
Total domestic sector gas use (UK) | 225063760000 | kWh
Number of homes with gas heating | 23525241.58
Proportion of homes with gas heating | 83.56%
Natural gas bill per household | 11733.6967 | kWh | cf 12,930 from the CHM (England only), OFGEM uses 12,000 as a typical consumption value.
Proportion of gas bill for space heating | 81.53% | kWh
Proportion of gas boilers that are regular boilers | 32% | EHSEnergy
Oil heating
Total domestic sector oil use (UK) | 2549.6025 | ktoe | ECUK | Table 3
| 29651877294.7015 | kWh
Total oil for domestic space heating (UK) | 2079 | ktoe | ECUK | Table 3
Total domestic sector oil use (UK) | 24178770000 | kWh
Number of homes with oil heating | 1510201.9
Proportion of homes with oil heating | 5.364%
Oil heating bill per household | 19634.3795 | kWh | cf 21000 from the CHM, England only
Proportion of oil bill for space heating | 81.54% |  | cf gas - this is the same.
Proportion of oil boilers that are regular boilers | 78% | EHSEnergy
Electric heating
Total domestic electricity for space heating | 1475 | ktoe | ECUK | Table 3
Total domestic electricity for water heating | 405 | ktoe | ECUK
Total domestic electricity for heating (UK) | 21864400000 | kWh
Proportion of electricty usage for heating that is in homes with ekectricity as the main heating (rather than electricity for supplementary heating) | 74% |  | CHM | Estimated from modelling the CHM - which is for England only. Storage heater homes use slightly more: 6980 compared to 6630 for other electric heating
Domestic electriciy for heating where electricity is the main fuel | 16179656000 | kWh
Number of homes with storage heaters | 1317747.6249
Number of homes with other electric heating | 826841.5151
Proportion of homes with storage heaters | 4.681%
Proportion of homes with other electric heaters | 2.937%
Electricity heating bill per household | 7544.4082 | kWh | cf 6890 from the CHM | Storage heater homes use slightly more: 6980 compared to 6630 for other electric heating
Domestic electricity for heating: storage heaters | 9941626052.0328 | kWh
Domestic electricity for heating: other electric heaters | 6238029947.9672 | kWh
By country assumptions - al numbers of dwellings
England
Population |  | 56550138
Dwellings |  | 23500000 |  | EHSEnergy2020
Mains gas heating | 86% | 20210000 |  | EHSEnergy2020
Oil heating | 3% | 705000 |  | EHSEnergy2020
Storage heaters | 4.4% | 1034000 |  | EHSEnergy2020
Other electric | 3% | 705000 |  | EHSEnergy2020 | This is the room heaters and the electric ceiling/underfloor heating systems.
| 96.4% |  |  |  | Note that this does not add up to 100%. It excludes communal heating systems and warm air systems.
Scotland
Population |  | 5466000
Dwellings |  | 2470000 |  | SHCS
Mains gas heating | 80.1% | 1978470 |  | SHCS
Oil heating | 5.6% | 138320 |  | SHCS
Storage heaters | 7.9% | 195130 |  | SHCS
Other electric | 2.9% | 71630 |  | SHCS
96.5%
Wales
Population |  | 5065096
Dwellings |  | 1403819 |  | StatsWales
Mains gas heating | 82% | 1151131.58 |  | WHCS
Oil heating | 10% | 140381.9 |  | WHCS
Storage heaters | 4% | 56152.76 |  | WHCS
Other electric | 2% | 28076.38 |  | WHCS
98%
N. Ireland
Population |  | 1895510
Dwellings |  | 780000 |  | IHCS | This is 2016 latest data | 2.4301
Mains gas heating | 23.8% | 185640 |  | IHCS
Oil heating | 67.5% | 526500 |  | IHCS
All electric heating | 7% |  |  | IHCS | A little less than the 7% 'other'
Storage heaters | 4.162% | 32464.8649 |  | Assume same proportion of storage heaters as in England
Other electric | 2.838% | 22135.1351
98.3%
UK Totals
Total Numbers of dwellings |  | 28153819
Total gas |  | 23525241.58
Total oil |  | 1510201.9
Total storage heaters |  | 1317747.6249
Total other electric |  | 826841.5151
96.54%

## Tariffs
Calculating tariffs for Gas and electricitiy based on OFGEM price caps |  |  |  |  | OFGEMCaps
All figures are for the standard credit tariff
Government Price Guarantee, which applies from October 2022
| Electricity | Electricity (multi-register) | Gas
| 34 | 34 | 10.3 | p/kWh | EnergyBillsSupport | The price guarantee does not mention a separate rate for multi-register tariffs (peak and off-peak rates). We have assumed it is the same as standard tariffs.
OFGEM tariffs Oct 2022
| Electricity - standard (3100 kWh/year) |  |  | Electricity - multi-register rate (4200 kWh/year) |  |  | Gas (12,000 kWh/year)
| Nil bill | Total |  | Nil bill | Total |  | Nil bill | Total
North West | 170.81 | 1766.8 |  | 171.09 | 2215.95 |  | 116.58 | 1892.61
Northern | 195.25 | 1752.79 |  | 195.53 | 2194.84 |  | 116.58 | 1877.29
Yorkshire | 193.83 | 1775.92 |  | 194.11 | 2224.29 |  | 116.58 | 1882.53
Northern Scotland | 199.43 | 1782.75 |  | 199.71 | 2235.45 |  | 116.58 | 1886.54
Southern | 175.03 | 1794.36 |  | 175.31 | 2248.79 |  | 116.58 | 1908.27
Southern Scotland | 197.93 | 1802.85 |  | 198.21 | 2253.54 |  | 116.58 | 1886.52
N Wales and Mersey | 190.36 | 1864.33 |  | 190.64 | 2325.92 |  | 116.58 | 1894.54
London | 133.79 | 1802 |  | 134.07 | 2262.71 |  | 116.58 | 1914.58
South East | 168.68 | 1821.86 |  | 168.96 | 2275.95 |  | 116.58 | 1888.76
Eastern | 154.96 | 1800.15 |  | 155.24 | 2253.72 |  | 116.58 | 1890.47
East Midlands | 179.99 | 1761.76 |  | 180.27 | 2209.59 |  | 116.58 | 1881.76
Midlands | 192.37 | 1796.16 |  | 192.65 | 2250.72 |  | 116.58 | 1893.43
Southern Western | 205.18 | 1813.13 |  | 205.46 | 2263.6 |  | 116.58 | 1904.51
S Wales | 192.45 | 1803.91 |  | 192.73 | 1159.07 |  | 116.58 | 1900.51
Average | 182.1471 | 1795.6264 |  | 182.4271 | 2169.5814 |  | 116.58 | 1893.0229
p/kWh |  | 52.0477 |  |  | 47.3132 |  |  | 14.8037
OFGEM tariffs April 2022
| Electricity - standard (3100 kWh/year) |  |  | Electricity - multi-register rate (4200 kWh/year) |  |  | Gas (12,000 kWh/year)
| Nil bill | Total |  | Nil bill | Total |  | Nil bill | Total
North West | 166.49 | 1037.86 |  | 166.76 | 1279.34 |  | 111.35 | 995.29
Northern | 190.93 | 1033.38 |  | 191.2 | 1270.95 |  | 111.35 | 981.22
Yorkshire | 189.51 | 1040.28 |  | 189.78 | 1280.83 |  | 111.35 | 987.77
Northern Scotland | 195.1 | 1062.93 |  | 195.37 | 1310.7 |  | 111.35 | 994.53
Southern | 170.7 | 1055.6 |  | 170.97 | 1298.91 |  | 111.35 | 1011.8
Southern Scotland | 193.61 | 1059.3 |  | 193.88 | 1300.5 |  | 111.35 | 994.5
N Wales and Mersey | 186.04 | 1106.07 |  | 186.31 | 1353.32 |  | 111.35 | 998.02
London | 129.47 | 1051 |  | 129.74 | 1297.59 |  | 111.35 | 1016.31
South East | 164.36 | 1081.28 |  | 164.63 | 1323.38 |  | 111.35 | 992.48
Eastern | 150.64 | 1059.96 |  | 150.91 | 1302.01 |  | 111.35 | 995.43
East Midlands | 175.67 | 1034.82 |  | 175.94 | 1275.02 |  | 111.35 | 988.03
Midlands | 188.05 | 1054.58 |  | 188.32 | 1297.98 |  | 111.35 | 998.24
Southern Western | 200.86 | 1084.31 |  | 201.13 | 1325.08 |  | 111.35 | 1011.39
S Wales | 188.13 | 1067.87 |  | 188.4 | 1312.13 |  | 111.35 | 1007.47
Average | 177.8257 | 1059.2314 |  | 178.0957 | 1301.9814 |  | 111.35 | 998.0343
p/kWh |  | 28.4324 |  |  | 26.7592 |  |  | 7.389

## References
References | Date | Title | Hyperlink (where available)
Bennett | 2018 (?) | The secret life of boilers: Dynamic performance of residential gas boilers heating systems – a modelling and empirical study by George James Bennett UCL Energy Institute Bartlett School of Environment, Energy and Resources Thesis submitted for the degree of Doctor of Philosophy in Energy and the Built Environmen | https://discovery.ucl.ac.uk/id/eprint/10065409/1/GJB_Thesis_postViva_v2_submission.pdf
BEISDistrib | 2021 | Domestic Heat Distribution Systems Evidence Gathering | https://www.gov.uk/government/publications/heat-storage-and-distribution-systems-hds
BoilerJuice | 2022 | UK Average Home Heating Oil Prices | https://www.boilerjuice.com/heating-oil-prices/
BREStock | 2020 | The Housing Stock of the United Kingdom | https://files.bregroup.com/bretrust/The-Housing-Stock-of-the-United-Kingdom_Report_BRE-Trust.pdf
NEST | 2017 | Evaluating the Nest Learning Thermostat | https://www.bi.team/wp-content/uploads/2017/11/311013-Evaluating-Nest-BIT-Exec-Tech-Summaries.pdf
BRE-controls | 2017 | Evidence Gathering - Compensation and TPI Heating Controls | https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/648337/heating-controls-compensation-tpi-bre.pdf
CIBSE | 2019 | Module 149: Effective control for condensing gas boiler systems | https://www.cibsejournal.com/cpd/modules/2019-07-gas/
ECUK | 2022-03-01 | Energy consumption in the UK | https://www.gov.uk/government/statistics/energy-consumption-in-the-uk-2021
EHSenergy | 2021 | English housing survey | https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/1055629/Energy_Report_2019-20.pdf
EHSEnergy2020 | 2021 | English Housing Survey energy report | https://www.gov.uk/government/statistics/english-housing-survey-2020-to-2021-energy
EnergyBillsSupport | 2022 | Energy bills support factsheet: 8 September 2022 | https://www.gov.uk/government/publications/energy-bills-support/energy-bills-support-factsheet-8-september-2022
GHGConv | 2020 | UK Government GHG Conversion Factors for Company Reporting | https://www.gov.uk/government/collections/government-conversion-factors-for-company-reporting
HeatGeekEff | 2018 | Benefits of low-temperature heating systems | https://www.heatgeek.com/benefits-of-low-temprature-heating-systems/
HHBCombi | 2022 | How to turn OFF the pre-heat on your Ideal combi boiler to save 5-10% | https://www.theheatinghub.co.uk/articles/Ideal-hot-water-preheat
HHIC | 2021 (?) | Heating up to net zero | https://www.hhic.org.uk/uploads/6165409B9D4C9.pdf
HistoricEngland | 2017 | Improving the Thermal Performance of Traditional Windows: Metal-framed Windows | https://historicengland.org.uk/research/results/reports/15-2017
IHCS | 2017 | Northern Ireland House Condition Survey 2016 | https://www.nihe.gov.uk/Working-With-Us/Research/House-Condition-Survey
Lomas-2018 | 2018 | Do domestic heating controls save energy? A review of the evidence | https://doi.org/10.1016/j.rser.2018.05.002
NEED | 2021 | National Energy Efficiency Data-Framework (NEED): Summary of Analysis, Great Britain, 2021 | https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/1008681/need-report-2021.pdf
OFGEMCaps | 2022 | Default tariff cap level: 1 April 2022 to 30 September 2022 | https://www.ofgem.gov.uk/publications/default-tariff-cap-level-1-april-2022-30-september-2022
ONSFamilies | 2021 | Families and households in the UK: 2020 | https://www.ons.gov.uk/peoplepopulationandcommunity/birthsdeathsandmarriages/families/bulletins/familiesandhouseholds/2020
ONSPop | 2021 | Estimates of the population for the UK, England and Wales, Scotland and Northern Ireland | https://www.ons.gov.uk/peoplepopulationandcommunity/populationandmigration/populationestimates/datasets/populationestimatesforukenglandandwalesscotlandandnorthernireland
ONSwellbeing | 2022 | Public opinions and social trends, Great Britain: 22 June to 3 July 2022 | https://www.ons.gov.uk/peoplepopulationandcommunity/wellbeing/bulletins/publicopinionsandsocialtrendsgreatbritain/22juneto3july2022
OpenTherm | 2022 | Opentherm boilers and controls | https://myboiler.com/opentherm/opentherm-boilers-and-controls/ "
Radflek | 2009 | Radflek - proposed CERT attributed savings - BRE | https://www.radflek.com/_webedit/uploaded-files/All%20Files/Radflek_FinalReport.pdf
SalfordTherm | 2021 | Assessing the energy savings from advanced room thermostat controls in a whole house test facility | https://www.beama.org.uk/resourceLibrary/salford-tests-on-load-and-weather-compensation-.html
SalfordCurtains | 2017 | The thermal performance of window coverings in a whole house test facility with single-glazed sash windows | http://dx.doi.org/10.1007/s12053-017-9529-0
SalfordFlow | 2022 | This data is not yet published
SAP10.2 | 2022 | The Government’s Standard Assessment Procedure for Energy Rating of Dwellings
StatsWales | 2022 | Council tax dwellings by local authorith | https://statswales.gov.wales/Catalogue/Local-Government/Finance/Council-Tax/Dwellings/counciltaxdwellings-by-localauthority
Veissman | 2022 | What temperature should a condensing boiler be set at? | https://www.viessmann.co.uk/heating-advice/what-temperature-to-set-condensing-boiler
WHCS | 2019 | Welsh Housing Conditions Survey 2017-18: Energy Efficiency of Dwellings | https://gov.wales/sites/default/files/statistics-and-research/2019-10/welsh-housing-conditions-survey-energy-efficiency-dwellings-april-2017-march-2018-795.pdf

## Modelling Notes
Notation
Data sources are indicated, using a key for the References tab where appropriate.
Modelling notes
Some of these estimates rely on energy use models. We have used two such models:
| 1. Cambridge Housing Model (CHM) | 2. CODE model
Housing data | Parameters derived from 12,300 homes in different regions of the UK from the Englush Housing Survey (2018/2019 data), weighted as in the EHS. | 12 archetypes of typical homes derived from English Housing Survey data, with weights derived from the EHS.
Energy model | Derived from SAP with some adjustments (in particular for thermostat settings) to make it representative of actual energy use. Static monthly calculations. | Basd on EnergyPlus, a detailed, dynamic model of buildling physics. Energy use is modelled over a year in intervals of 10 minutes.
Weather | Weather is typical for each region. | We used weather for a single location that represents 'average' UK weather (near Sheffield).
Advantages | Large stock dataset allows for good estimates of the range of outcomes. | Can simulate aspects of building physics that are not represented in the CHM.
Disadvantages | Simple energy model with heuristics for the effects of complex physics or timing/thermal mass effects. | Small set of 12 representative archetypes.

## Change Log
Changes
v7 | Moved asumptions about gas bill to assumptions sheet from the closing curtains sheet
Attempt at similar calculations for electric homes
Added reducing heating hours
Added moving furniture
Added windows treatments
v8 | New sections combi keep hot
Name fixes on the assumptions sheet - numberDwellingsUK is not the same as numberDwellings
Formula fix in reducing radiator temp numberDwellings->numberDwellingsUK
Fix on summary sheet for oil/reducing heating hours £
v9 | New sections foil
redone the curtains based on window area
v10 | Tidying and checking
v11 | Tidying and checking
v12 | Changed loft insulation to be all up to 300mm
Also put more cases onto the summary sheet
v14 | Bug fixes Added smart thermostats, load and weather compensation
Added a line for each measure on what sort of homes can adopt it.
Updated tariffs for from 1/10/2022
v15 | New results from the Salford test house
New format Summary
Added packages on Summary
Changed factors for microbore pipework on reducing radiator temperature
Allow for useful gains in calculation of lower DHW temperature for combi boilers
v16 | New data on Welsh dwellings in Assumptions
Adjustments to Northern Ireland dwellings and by heating type
Added notes on heating types not covered in the assumptions
Clarified target temperatures for DHW savings in combi boilers
Added new data and notes on Salford study/higher internal temps
Adjustment and correction to proportion of homes that can reduce flow temperatures
Added a note on additional savings from reducing flow temperatures where thermal comfort decrease is acceptable
Clarified assumptions and counterfactual for TRVs
Added guidance on how to adjust the packages
v16c | Updated adoption parameters for Changed radiator temps
Updated tariffs based on the price guarantee
Updated the proportional savings on the loft insulation measures to be calculated directlly from the CHM instead of based on the overall typical bill
v16f | Added results from ESC to Reducing radiator temperatures
Added gas savings for Reducing radiator temperatures to the final list
Activities |  |  | status
Reducing radiator temp |  |  | done
Reducing DHW temperature |  |  | draft
Closing curtains |  |  | Redone for per-window area. Poss add thermal curtains?
reducing heating hours |  |  | done
Moving furniture away from radiators |  |  | done
Turning off combi keep hot |  |  | done
Window treatments |  |  | done | By window area, then prop single/double
Foil |  |  | done | %age of space heaitng
TRVs |  |  | draft | as reduced heating hours
Smart thermostats |  |  | draft | as reduced heating hours
Modulating thermostat/weather or load compensation |  |  | draft | as reduced heating hours
DIY loft insulation |  |  | done
Bug fix
version | sheet | row | change
13 | Turn off Keephot | 18 | Low savings are from low space heating efficiency: low and high were the wrong way round
13 | Turn off Keephot | 37 | Low savings are from 16 hours keephot, high savings from only 8 hours keephot. This affects the text only.
13 | Turn off Keephot | 43 | Low savings are from 16 hours keephot, high savings from only 8 hours keephot. This affects the text only.
13 | Reducing heating hours | 58 | reformatted as a calculated row
14 | Reducing radiator temperature | 56 | Fixed proportion of homes with gas boilers on Reducing DHW temperature
14 | Turn off per-heat |  | change 'keep-hot' to 'pre-heat'. Also removed mentions of internal storage as that is not relevenat.
14 | Summary2 |  | Added this sheet, with an alternative summary format. Some other sheets changed to generate data for this sheet.
15 | Summary2 is now summary